## INFO
This spreadsheet is distributed to stakeholders of the Smart Readiness Indicator For more information, visit www.smartreadinessindicator.eu/testing-sri
It contains following tabs:
* Building Information | Mandatory: Use this sheet to provide general information on the building and its technical building systems.
* Calculation Sheet | Mandatory: Use this sheet to indicate the functionality level for each service
* Results | Informative: this sheet presents the calculation results
* Weightings | Informative: Only change this sheet if you wish to provide user-defined weighting factors
* Overview_of_services | Informative: This is list with all smart ready services and their functionality levels. Column L indicates whether the services are part of the proposed streamlined set
* Feedback | Mandatory: please use this tab to provide us with your feedback on the assessment
* tabs for the various domains: heating, dhw, cooling, etc. | Informative: These tabs provide further details on the various services, including the provisional impact scores for each of the service levels
Instructions
Input fields: use these yellow input fields to provide the requested information
All other fields: all other fields are filled automatically and cannot be edited
List of abbreviations
BACS | Building Automation and Control System
CHP | Combined Heat and Power
CW | Cold Water
DHW | Domestic Hot Water
DR | Demand Response
DSM | Demand Side Management
EV | Electric Vehicle
HW | Hot Water
IAQ | Indoor Air Quality
RES | Renewable Energy Source
SOC | State Of Charge
TABS | Thermally Activated Building Systems
TBS | Technical Building System
TES | Thermal Energy Storage
VOC | Volatile Organic Compounds

## Building Information
Smart Readiness Indicator for Buildings
ASSESSOR INFORMATION
| Name | Risto Kosonen
| Organisation | Aalto U
Contact information
e-mail address
telephone number (optional)
GENERAL BUILDING INFORMATION
| Building type | non_residential
| Building usage | educational
| Location | Finland
| climate zone: | North Europe
Net floor area of the building
Year of construction
Building state
Please provide a brief description of the building
Address:
| Preferred weightings | Default
TRIAGE PROCESS
Are the following technical building systems present in your building?
If not, are they mandatory for new constructions in your country of residence? (1)
present?
| Heating system | yes
| Domestic Hot Water | yes
| Cooling system | yes
| Controlled ventilation | yes
| Lighting | yes
| Dynamic Envelope: automated windows & blinds | Yes
| Electricity: renewables & storage | yes
| Electric Vehicle Charging | yes
(1) This selection will be automated in the final version, option should not be available for assessors
HEATING
| Emission type | Other hydronic system (e.g. radiators)
| Production type | Heat Pump
| Thermal energy storage | Storage present
| Multiple heat generators | Multiple generators
DOMESTIC HOT WATER
| Production type | Non-electric
| Storage present | No storage present
| Solar collector | No solar collector present
COOLING
| Emission type | Other hydronic system (e.g. radiators)
| Thermal energy storage | Storage present
| Multiple generators | Multiple generators
CONTROLLED VENTILATION
| System type | Mechanical ventilation
| Heat recovery | Heat recovery
| Space heating | Not used for space heating
System sub-type
DYNAMIC ENVELOPE
| Movable shades, screens or blinds | Present
ELECTRICITY: renewables & storage
| On-site renewable electricity generation | On-site renewable electricity generation
| Storage of on-site generated renewable electricity | No storage present
| CHP (Combined Heat and Power) | No CHP
ELECTRIC VEHICLE CHARGING
| On-site parking spots | On-site parking
| Electric vehicle charging spots | EV charging

## Calculation Sheet
SR fields | [16 empty] | TRIAGE CHECKS | [8 empty] | ORDINAL IMPACT SCORES - main functionality | [7 empty] | ORDINAL IMPACT SCORES - additional functionality | [8 empty] | Impact weightings by domain | [6 empty] | SRI impact scores by domain | [6 empty] | SRI impact scores by domain - additional functionality | [7 empty] | SRI impact scores by domain after impact weightings also applied | [9 empty] | MAXIMUM POSSIBLE ORDINAL IMPACT SCORES | [6 empty] | Maximum possible SRI impact scores by domain | [7 empty] | Maximum possible SRI impact scores by domain after impact weightings also applied | [7 empty] | Normalised SRI impact scores by domain after impact weightings also applied
|  | building type --> | non_residential |  |  |  |  | 0 | 0 | 1 | 2 | 3 | 4 | [10 empty] | 18 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | [7 empty] | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |  |  | 18 | 19 | 20 | 21 | 22 | 23 | 24 | [8 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8
Domain | Code |  | Service | Main functionality level as inspected by SRI assessor | share (default = 100% means applicable throughout the building) | Optional: additional functionality level in part of the building | Share of additional functionality level | Warnings | Functionality level 0 (as non-smart default) | Functionality level 1 | Functionality level 2 | Functionality level 3 | Functionality level 4 | Service to be assessed? | ESTIMATED ASSESSMENT TIME (minutes) | OPTIONAL ASSESSORS COMMENTS | Always to be assesed or triage? | Domain present or absent but mandatory? | Included in max. score? | Resulting main functionality level for this building | Resulting additional functionality level for this building | Max possible functionality level | Max functionality level in this building | tab | line NR | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | line NR | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | tab | line NR | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | line NR | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | Total |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | line NR | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | Total | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | Maintenance & fault prediction | information to occupants | SRI score
Totals | [24 empty] | 4 | 55 | 7 | 33 | 36 | 12 | 12 | 16 |  | 0 | -2 | 0 | 0 | 0 | 0 | 0 |  | 49 | [7 empty] | 9.9856 | 1.4969 | 4.6 | 4.3 | 3.8 | 2.1839 | 2.2571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6643 | 0.49896 | 0.38333 | 0.35833 | 0.31667 | 0.36398 | 0.1881 | 3.7736 |  |  | 72 | 22 | 43 | 59 | 16 | 26 | 33 | 12.6955 | 2.9375 | 5.9333 | 7 | 4.6 | 3.9855 | 4.7143 |  | 2.1159 | 0.97916 | 0.49444 | 0.58333 | 0.38333 | 0.66425 | 0.39286 | 5.6133 | 0.78654 | 0.50958 | 0.77528 | 0.61429 | 0.82609 | 0.54796 | 0.47879 | 67.23%
Heating | Heating-1a | Heat control - demand side | Heat emission control | 3 | 100% | 0 | 0% |  | No automatic control | Central automatic control (e.g. central thermostat) | Individual room control (e.g. thermostatic valves, or electronic controller) | Individual room control with communication between controllers and to BACS | Individual room control with communication and presence control | 1 |  |  | triage | 1 | 1 | 3 | 0 | 4 | 4 | heating | 11 | 2 | 0 | 2 | 3 | 0 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0.62127 | 0 | 0.26667 | 0.3 | 0 | 0.31063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.10354 | 0 | 0.022222 | 0.025 | 0 | 0.051772 | 0 |  | heating | 12 | 3 | 0 | 2 | 3 | 0 | 1 | 0 | 0.9319 | 0 | 0.26667 | 0.3 | 0 | 0.31063 | 0 | 67 | 0.15532 | 0 | 0.022222 | 0.025 | 0 | 0.051772 | 0
Heating | Heating-1b | Heat control - demand side | Emission control for TABS (heating mode) | 3 | 90% | 0 | 10% |  | No automatic control | Central automatic control | Advanced central automatic control | Advanced central automatic control with intermittent operation and/or room temperature feedback control |  | 0 |  |  | triage | 1 | 0 | 0 | 0 | 3 | 0 | heating | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | heating | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | Heating-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | 2 | 100% | 0 | 0% |  | No automatic control | Outside temperature compensated control | Demand based control |  |  | 1 |  |  | triage | 1 | 1 | 2 | 0 | 2 | 2 | heating | 38 | 2 | 0 | 1 | 2 | 0 | 1 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0.62127 | 0 | 0.13333 | 0.2 | 0 | 0.31063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.10354 | 0 | 0.011111 | 0.016667 | 0 | 0.051772 | 0 |  | heating | 38 | 2 | 0 | 1 | 2 | 0 | 1 | 0 | 0.62127 | 0 | 0.13333 | 0.2 | 0 | 0.31063 | 0 | 67 | 0.10354 | 0 | 0.011111 | 0.016667 | 0 | 0.051772 | 0
Heating | Heating-1d | Heat control - demand side | Control of distribution pumps in networks | 3 | 100% | 0 | 0% |  | No automatic control | On off control | Multi-Stage control | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (external demand signal) | 1 |  |  | triage | 1 | 1 | 3 | 0 | 4 | 4 | heating | 53 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0.9319 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.15532 | 0 | 0.033333 | 0 | 0 | 0 | 0 |  | heating | 54 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0.9319 | 0 | 0.4 | 0 | 0 | 0 | 0 | 67 | 0.15532 | 0 | 0.033333 | 0 | 0 | 0 | 0
Heating | Heating-1e | Heat control - demand side | Intermittent control of emission and/or distribution - One controller can control different rooms/zones having same occupancy patterns | 2 | 100% | 0 | 0% |  | No automatic control | Automatic control with fixed time program | Automatic control with optimum start/stop | Automatic control with demand evaluation |  | 1 |  |  | always | 1 | 1 | 2 | 0 | 3 | 3 | heating | 66 | 2 | 0 | 2 | 2 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0.62127 | 0 | 0.26667 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.10354 | 0 | 0.022222 | 0.016667 | 0 | 0 | 0 |  | heating | 67 | 3 | 0 | 3 | 3 | 0 | 0 | 0 | 0.9319 | 0 | 0.4 | 0.3 | 0 | 0 | 0 | 67 | 0.15532 | 0 | 0.033333 | 0.025 | 0 | 0 | 0
Heating | Heating-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | 0 | 100% | 0 | 0% |  | Continuous storage operation | Time-scheduled storage operation | Load prediction based storage operation |  |  | 1 |  |  | triage | 1 | 1 | 0 | 0 | 2 | 2 | heating | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | heating | 80 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0.62127 | 0 | 0.13333 | 0 | 0 | 0 | 0 | 67 | 0.10354 | 0 | 0.011111 | 0 | 0 | 0 | 0
Heating | Heating-1g | Heat control - demand side | Building preheating control | 1 | 100% | 0 | 0% |  | No automatic control | Program heating schedule in advance | Thermostat self-learning user behavior (presence, setpoint) |  |  | 1 |  |  | always | 1 | 1 | 1 | 0 | 2 | 2 | heating | 93 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0.31063 | 0 | 0.13333 | 0.1 | 0 | 0 | 0.11429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.051772 | 0 | 0.011111 | 0.0083333 | 0 | 0 | 0.0095238 |  | heating | 94 | 2 | 0 | 2 | 2 | 0 | 0 | 1 | 0.62127 | 0 | 0.26667 | 0.2 | 0 | 0 | 0.11429 | 67 | 0.10354 | 0 | 0.022222 | 0.016667 | 0 | 0 | 0.0095238
Heating | Heating-2a | Control heat production facilities | Heat generator control (all except heat pump) |  | 100% | 0 | 0% |  | Constant temperature control | Variable temperature control depending on outdoor temperature | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) |  |  | 0 |  |  | triage | 1 | 0 | 0 | 0 | 2 | 0 | heating | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | heating | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | Heating-2b | Control heat production facilities | Heat generator control (for heat pumps) | 3 | 100% | 0 | 0% |  | On/Off-control of heat generator | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | Variable control of heat generator capacity depending on the load AND external signals from grid |  | 1 |  |  | triage | 1 | 1 | 3 | 0 | 3 | 3 | heating | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | heating | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heating | Heating-2c | Control heat production facilities | Heat system control according to external signal (e.g. electricity tariff, gas pricing, load shedding signal etc.) | 2 | 100% | 0 | 0% |  | No automatic control based on external signals | Heat system control according to external signals (tariff, availability of renewables, etc.) | Heat system control according to external signals combined with internal signals (predicted demand, temperature etc.) |  |  | 1 |  |  | always | 1 | 1 | 2 | 0 | 2 | 2 | heating | 136 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0.62127 | 0.57985 | 0.13333 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.10354 | 0.19328 | 0.011111 | 0.0083333 | 0 | 0 | 0 |  | heating | 136 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 0.62127 | 0.57985 | 0.13333 | 0.1 | 0 | 0 | 0 | 67 | 0.10354 | 0.19328 | 0.011111 | 0.0083333 | 0 | 0 | 0
Heating | Heating-2d | Control heat production facilities | Sequencing of different heat generators | 4 | 100% | 0 | 0% |  | Priorities only based on running time | Control according to fixed priority list: e.g. heat pump prior to hot water boiler | Control according to dynamic priority list (based on current efficiency and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Control according to dynamic priority list (based on current AND predicted load, efficiency and capacity of generators) | Control according to dynamic priority list (based on current AND predicted load, efficiency, capacity of generators AND external signals from grid) | 1 |  |  | triage | 1 | 1 | 4 | 0 | 4 | 4 | heating | 152 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0.9319 | 0.57985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.15532 | 0.19328 | 0 | 0 | 0 | 0 | 0 |  | heating | 152 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0.9319 | 0.57985 | 0 | 0 | 0 | 0 | 0 | 67 | 0.15532 | 0.19328 | 0 | 0 | 0 | 0 | 0
Heating | Heating-3 | Information to occupants and facility managers | Report information regarding heating system performance | 3 | 100% | 0 | 0% |  | None | Indication of actual values (e.g. temperatures, submetering energy usage) | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 |  |  | always | 1 | 1 | 3 | 0 | 4 | 4 | heating | 179 | 1 | 0 | 0 | 0 | 0 | 1 | 3 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 54 | 31.06% | 28.99% | 13.33% | 10% | 0% | 31.06% | 11.43% | 0.31063 | 0 | 0 | 0 | 0 | 0.31063 | 0.34286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.051772 | 0 | 0 | 0 | 0 | 0.051772 | 0.028571 |  | heating | 180 | 1 | 0 | 0 | 1 | 0 | 2 | 3 | 0.31063 | 0 | 0 | 0.1 | 0 | 0.62127 | 0.34286 | 67 | 0.051772 | 0 | 0 | 0.0083333 | 0 | 0.10354 | 0.028571
| DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) |  | 100% | 0 | 0% |  | Automatic control on / off | Automatic control on / off and scheduled charging enable | Automatic control on / off and scheduled charging enable and multi-sensor storage management | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) |  | 0 |  |  | triage | 1 | 0 | 0 | 0 | 3 | 0 | dhw | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 5.443% | 5.08% | 13.33% | 10% | 0% | 5.443% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | dhw | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) |  | 100% | 0 | 0% |  | Automatic control on / off | Automatic control on / off and scheduled charging enable | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | Automatic charging control based on signals from district heating grid (DR, DSM) |  | 0 |  |  | triage | 1 | 0 | 0 | 0 | 3 | 0 | dhw | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 5.443% | 5.08% | 13.33% | 10% | 0% | 5.443% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | dhw | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) |  | 100% | 0 | 0% |  | Manual selected control of solar energy or heat generation | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management |  | 0 |  |  | triage | 1 | 0 | 0 | 0 | 3 | 0 | dhw | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 5.443% | 5.08% | 13.33% | 10% | 0% | 5.443% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | dhw | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | 1 | 100% | 0 | 0% |  | None | Indication of actual values (e.g. temperatures, submetering energy usage) | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 |  |  | always | 1 | 1 | 1 | 0 | 4 | 4 | dhw | 79 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 55 | 5.443% | 5.08% | 13.33% | 10% | 0% | 5.443% | 11.43% | 0.05443 | 0 | 0 | 0 | 0 | 0.05443 | 0.11429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.0090717 | 0 | 0 | 0 | 0 | 0.0090717 | 0.0095238 |  | dhw | 82 | 1 | 0 | 0 | 1 | 0 | 2 | 3 | 0.05443 | 0 | 0 | 0.1 | 0 | 0.10886 | 0.34286 | 67 | 0.0090717 | 0 | 0 | 0.0083333 | 0 | 0.018143 | 0.028571
Domestic hot water | Cooling-1a | Cooling control - demand side | Cooling emission control | 4 | 100% | 0 | 0% |  | No automatic control | Central automatic control | Individual room control REF | Individual room control with communication between controllers and to BACS | Individual room control with communication and presence control | 1 |  |  | triage | 1 | 1 | 4 | 0 | 4 | 4 | cooling | 12 | 3 | 0 | 2 | 3 | 0 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 9.34% | 8.718% | 13.33% | 10% | 0% | 9.34% | 11.43% | 0.28021 | 0 | 0.26667 | 0.3 | 0 | 0.093403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.046702 | 0 | 0.022222 | 0.025 | 0 | 0.015567 | 0 |  | cooling | 12 | 3 | 0 | 2 | 3 | 0 | 1 | 0 | 0.28021 | 0 | 0.26667 | 0.3 | 0 | 0.093403 | 0 | 67 | 0.046702 | 0 | 0.022222 | 0.025 | 0 | 0.015567 | 0
Domestic hot water | Cooling-1b | Cooling control - demand side | Emission control for TABS (cooling mode) |  | 100% | 0 | 0% |  | No automatic control | Central automatic control | Advanced central automatic control | Advanced central automatic control with intermittent operation and/or room temperature feedback control |  | 0 |  |  | triage | 1 | 0 | 0 | 0 | 3 | 0 | cooling | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 9.34% | 8.718% | 13.33% | 10% | 0% | 9.34% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | cooling | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | 2 | 100% | 0 | 0% |  | Constant temperature control | Outside temperature compensated control | Demand based control |  |  | 1 |  |  | triage | 1 | 1 | 2 | 0 | 2 | 2 | cooling | 38 | 2 | 0 | 2 | 2 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 9.34% | 8.718% | 13.33% | 10% | 0% | 9.34% | 11.43% | 0.18681 | 0 | 0.26667 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.031134 | 0 | 0.022222 | 0.016667 | 0 | 0 | 0 |  | cooling | 38 | 2 | 0 | 2 | 2 | 0 | 0 | 0 | 0.18681 | 0 | 0.26667 | 0.2 | 0 | 0 | 0 | 67 | 0.031134 | 0 | 0.022222 | 0.016667 | 0 | 0 | 0
| Cooling-1d | Cooling control - demand side | Control of distribution pumps in networks | 4 | 100% | 0 | 0% |  | No automatic control | On off control | Multi-Stage control | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (external demand signal) | 1 |  |  | triage | 1 | 1 | 4 | 0 | 4 | 4 | cooling | 54 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 9.34% | 8.718% | 13.33% | 10% | 0% | 9.34% | 11.43% | 0.28021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.046702 | 0 | 0 | 0 | 0 | 0 | 0 |  | cooling | 54 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28021 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.046702 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | Cooling-1e | Cooling control - demand side | Intermittent control of emission and/or distribution | 2 | 100% | 0 | 0% |  | No automatic control | Automatic control with fixed time program | Automatic control with optimum start/stop | Automatic control with demand evaluation |  | 1 |  |  | always | 1 | 1 | 2 | 0 | 3 | 3 | cooling | 66 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 9.34% | 8.718% | 13.33% | 10% | 0% | 9.34% | 11.43% | 0.18681 | 0 | 0.13333 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.031134 | 0 | 0.011111 | 0.0083333 | 0 | 0 | 0 |  | cooling | 67 | 3 | 0 | 1 | 1 | 0 | 0 | 0 | 0.28021 | 0 | 0.13333 | 0.1 | 0 | 0 | 0 | 67 | 0.046702 | 0 | 0.011111 | 0.0083333 | 0 | 0 | 0
Cooling | Cooling-1f | Cooling control - demand side | Interlock between heating and cooling control of emission and/or distribution | 2 | 100% | 0 | 0% |  | No interlock | Partial interlock (dependant of the HVAC system) | Total interlock |  |  | 1 |  |  | always | 1 | 1 | 2 | 0 | 2 | 2 | cooling | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 9.34% | 8.718% | 13.33% | 10% | 0% | 9.34% | 11.43% | 0.28021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.046702 | 0 | 0 | 0 | 0 | 0 | 0 |  | cooling | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28021 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.046702 | 0 | 0 | 0 | 0 | 0 | 0
Cooling | Cooling-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | 1 | 100% | 0 | 0% |  | Continuous storage operation | Time-scheduled storage operation | Load prediction based storage operation |  |  | 1 |  |  | triage | 1 | 1 | 1 | 0 | 2 | 2 | cooling | 93 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 9.34% | 8.718% | 13.33% | 10% | 0% | 9.34% | 11.43% | 0.093403 | 0 | 0.13333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.015567 | 0 | 0.011111 | 0 | 0 | 0 | 0 |  | cooling | 94 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0.18681 | 0 | 0.13333 | 0 | 0 | 0 | 0 | 67 | 0.031134 | 0 | 0.011111 | 0 | 0 | 0 | 0
Cooling | Cooling-2a | Control cooling production facilities | Generator control for cooling | 2 | 100% | 0 | 0% |  | Constant temperature control | Variable temperature control depending on outdoor temperature | Variable temperature control depending on the load |  |  | 1 |  |  | always | 1 | 1 | 2 | 0 | 2 | 2 | cooling | 109 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 9.34% | 8.718% | 13.33% | 10% | 0% | 9.34% | 11.43% | 0.18681 | 0 | 0.26667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.031134 | 0 | 0.022222 | 0 | 0 | 0 | 0 |  | cooling | 109 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0.18681 | 0 | 0.26667 | 0 | 0 | 0 | 0 | 67 | 0.031134 | 0 | 0.022222 | 0 | 0 | 0 | 0
Cooling | Cooling-2b | Control cooling production facilities | Sequencing of different cooling generators | 1 | 100% | 0 | 0% |  | Priorities only based on running times | Priorities only based on loads | Priorities based on generator efficiency and characteristics | Load prediction based sequencing |  | 1 |  |  | triage | 1 | 1 | 1 | 0 | 3 | 3 | cooling | 122 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 9.34% | 8.718% | 13.33% | 10% | 0% | 9.34% | 11.43% | 0.093403 | 0.087176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.015567 | 0.029059 | 0 | 0 | 0 | 0 | 0 |  | cooling | 124 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0.093403 | 0.087176 | 0 | 0 | 0 | 0 | 0 | 67 | 0.015567 | 0.029059 | 0 | 0 | 0 | 0 | 0
Cooling | Cooling-3 | Information to occupants and facility managers | Report information regarding cooling system performance | 3 | 100% | 0 | 0% |  | None | Indication of actual values (e.g. temperatures, submetering energy usage) | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 |  |  | always | 1 | 1 | 3 | 0 | 4 | 4 | cooling | 138 | 1 | 0 | 0 | 0 | 0 | 1 | 3 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 56 | 9.34% | 8.718% | 13.33% | 10% | 0% | 9.34% | 11.43% | 0.093403 | 0 | 0 | 0 | 0 | 0.093403 | 0.34286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.015567 | 0 | 0 | 0 | 0 | 0.015567 | 0.028571 |  | cooling | 139 | 1 | 0 | 0 | 1 | 0 | 2 | 3 | 0.093403 | 0 | 0 | 0.1 | 0 | 0.18681 | 0.34286 | 67 | 0.015567 | 0 | 0 | 0.0083333 | 0 | 0.031134 | 0.028571
Cooling | Ventilation-1a | Air flow control | Supply air flow control at the room level | 3 | 100% | 0 | 0% |  | No ventilation system or manual control | Clock control | Occupancy detection control | Central Demand Control based on air quality sensors (CO2, VOC,...) | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | 1 |  |  | always | 1 | 1 | 3 | 0 | 4 | 4 | ventilation | 11 | 2 | 0 | 3 | 3 | 3 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 19.46% | 18.16% | 13.33% | 10% | 40% | 19.46% | 11.43% | 0.38919 | 0 | 0.4 | 0.3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.064865 | 0 | 0.033333 | 0.025 | 0.1 | 0 | 0 |  | ventilation | 12 | 3 | 0 | 3 | 3 | 3 | 0 | 0 | 0.58378 | 0 | 0.4 | 0.3 | 1.2 | 0 | 0 | 67 | 0.097297 | 0 | 0.033333 | 0.025 | 0.1 | 0 | 0
Cooling | Ventilation-1b | Air flow control | Adjust the outdoor air flow or exhaust air rate | 3 | 100% | 0 | 0% |  | Fixed OA ratio / OA flow | Staged (low/high) OA ratio / OA flow (time schedule) | Staged (low/high) OA ratio / OA flow (presence) | Variable control |  | 1 |  |  | always | 1 | 1 | 3 | 0 | 3 | 3 | ventilation | 25 | 2 | 0 | 2 | 2 | 2 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 19.46% | 18.16% | 13.33% | 10% | 40% | 19.46% | 11.43% | 0.38919 | 0 | 0.26667 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.064865 | 0 | 0.022222 | 0.016667 | 0.066667 | 0 | 0 |  | ventilation | 25 | 2 | 0 | 2 | 2 | 2 | 0 | 0 | 0.38919 | 0 | 0.26667 | 0.2 | 0.8 | 0 | 0 | 67 | 0.064865 | 0 | 0.022222 | 0.016667 | 0.066667 | 0 | 0
| Ventilation-1c | Air flow control | Air flow or pressure control at the air handler level | 3 | 100% | 0 | 0% |  | No automatic control | On off time control | Multi-stage control | Automatic flow or pressure control (without reset) | Automatic flow or pressure control (with reset) | 1 |  |  | triage | 1 | 1 | 3 | 0 | 4 | 4 | ventilation | 39 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 19.46% | 18.16% | 13.33% | 10% | 40% | 19.46% | 11.43% | 0.58378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.097297 | 0 | 0 | 0 | 0 | 0 | 0 |  | ventilation | 40 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58378 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.097297 | 0 | 0 | 0 | 0 | 0 | 0
| Ventilation-2a | Air temperature control | Room air temp. control (all-air systems) |  | 100% | 0 | 0% |  | on-off capacity control | variable capacity control | Demand control |  |  | 0 |  |  | triage | 1 | 0 | 0 | 0 | 2 | 0 | ventilation | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 19.46% | 18.16% | 13.33% | 10% | 40% | 19.46% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | ventilation | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical ventilation | Ventilation-2c | Air temperature control | Heat recovery control: prevention of overheating | 2 | 100% | 0 | 0% |  | Without overheating control | Modulate or bypass heat recovery based on sensors in air exhaust | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control |  |  | 1 |  |  | triage | 1 | 1 | 2 | 0 | 2 | 2 | ventilation | 81 | 2 | 0 | 2 | 2 | 2 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 19.46% | 18.16% | 13.33% | 10% | 40% | 19.46% | 11.43% | 0.38919 | 0 | 0.26667 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.064865 | 0 | 0.022222 | 0.016667 | 0.066667 | 0 | 0 |  | ventilation | 81 | 2 | 0 | 2 | 2 | 2 | 0 | 0 | 0.38919 | 0 | 0.26667 | 0.2 | 0.8 | 0 | 0 | 67 | 0.064865 | 0 | 0.022222 | 0.016667 | 0.066667 | 0 | 0
Mechanical ventilation | Ventilation-2d | Air temperature control | Supply air temperature control |  | 100% | 0 | 0% |  | No automatic control | Constant set point | Variable set point with outdoor temperature compensation | Variable set point with load dependant compensation |  | 0 |  |  | triage | 1 | 0 | 0 | 0 | 3 | 0 | ventilation | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 19.46% | 18.16% | 13.33% | 10% | 40% | 19.46% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | ventilation | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical ventilation | Ventilation-3 | Free cooling | Free cooling with mechanical ventilation system | 2 | 100% | 0 | 0% |  | No automatic control | Night cooling | Free cooling | H,x- directed control |  | 1 |  |  | triage | 1 | 1 | 2 | 0 | 3 | 3 | ventilation | 109 | 2 | 0 | 2 | 2 | 1 | 0 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 19.46% | 18.16% | 13.33% | 10% | 40% | 19.46% | 11.43% | 0.38919 | 0 | 0.26667 | 0.2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.064865 | 0 | 0.022222 | 0.016667 | 0.033333 | 0 | 0 |  | ventilation | 110 | 3 | 0 | 2 | 2 | 1 | 0 | 0 | 0.58378 | 0 | 0.26667 | 0.2 | 0.4 | 0 | 0 | 67 | 0.097297 | 0 | 0.022222 | 0.016667 | 0.033333 | 0 | 0
Mechanical ventilation | Ventilation-6 | Feedback - Reporting information | Reporting information regarding IAQ | 1 | 100% | 0 | 0% |  | None | Air quality sensors (e.g. CO2) and real time autonomous monitoring | Real time monitoring & historical information of IAQ available to occupants | Real time monitoring & historical information of IAQ available to occupants + fault/maintenance detection based on internal sensors | Real time monitoring, historical & predictive information of IAQ (incl. external data eg outside temperature, ambient air…) available to occupants + fault/maintenance detection based on internal sensors and historical data | 1 |  |  | always | 1 | 1 | 1 | 0 | 4 | 4 | ventilation | 150 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 57 | 19.46% | 18.16% | 13.33% | 10% | 40% | 19.46% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0.19459 | 0.11429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0.032432 | 0.0095238 |  | ventilation | 153 | 0 | 0 | 0 | 1 | 0 | 2 | 3 | 0 | 0 | 0 | 0.1 | 0 | 0.38919 | 0.34286 | 67 | 0 | 0 | 0 | 0.0083333 | 0 | 0.064865 | 0.028571
Mechanical ventilation | Lighting-1a | Artificial lighting control | Occupancy control for indoor lighting | 3 | 100% | 0 | 0% |  | Manual on/off switch | Manual on/off switch + additional sweeping extinction signal | Automatic detection (auto on / dimmed or auto off) | Automatic detection (manual on / dimmed or auto off) |  | 1 |  |  | always | 1 | 1 | 3 | 0 | 3 | 3 | lighting | 11 | 2 | 0 | 2 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 58 | 8.076% | 7.538% | 13.33% | 10% | 0% | 8.076% | 0% | 0.16152 | 0 | 0.26667 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.026921 | 0 | 0.022222 | 0.016667 | 0 | 0 | 0 |  | lighting | 11 | 2 | 0 | 2 | 2 | 0 | 0 | 0 | 0.16152 | 0 | 0.26667 | 0.2 | 0 | 0 | 0 | 67 | 0.026921 | 0 | 0.022222 | 0.016667 | 0 | 0 | 0
Mechanical ventilation | Lighting-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | 2 | 100% | 0 | 0% |  | Manual (central) | Manual (per room / zone) | Automatic switching | Automatic dimming | Scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks) | 1 |  |  | always | 1 | 1 | 2 | 0 | 4 | 4 | lighting | 38 | 2 | 0 | 1 | 1 | 1 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 58 | 8.076% | 7.538% | 13.33% | 10% | 0% | 8.076% | 0% | 0.16152 | 0 | 0.13333 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.026921 | 0 | 0.011111 | 0.0083333 | 0 | 0 | 0 |  | lighting | 40 | 3 | 0 | 3 | 3 | 3 | 0 | 0 | 0.24229 | 0 | 0.4 | 0.3 | 0 | 0 | 0 | 67 | 0.040381 | 0 | 0.033333 | 0.025 | 0 | 0 | 0
Mechanical ventilation | DE-1 | Window control | Window solar shading control | 0 | 100% | 0 | 0% |  | No sun shading or only manual operation | Motorized operation with manual control | Motorized operation with automatic control based on sensor data | Combined light/blind/HVAC control | Predictive blind control (e.g. based on weather forecast) | 1 |  |  | triage | 1 | 1 | 0 | 0 | 4 | 4 | DE | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 60 | 5% | 5% | 13.33% | 10% | 40% | 5% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DE | 12 | 3 | 0 | 3 | 3 | 1 | 0 | 0 | 0.15 | 0 | 0.4 | 0.3 | 0.4 | 0 | 0 | 67 | 0.025 | 0 | 0.033333 | 0.025 | 0.033333 | 0 | 0
Mechanical ventilation | DE-2 | Window control | Window open/closed control, combined with HVAC system | 0 | 100% | 0 | 0% |  | Manual operation or only fixed windows | Open/closed detection to shut down heating or cooling systems | Level 1 + Automised mechanical window opening based on room sensor data | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling |  | 1 |  |  | triage | 1 | 1 | 0 | 0 | 3 | 3 | DE | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 60 | 5% | 5% | 13.33% | 10% | 40% | 5% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DE | 25 | 2 | 0 | 2 | 2 | 1 | 0 | 0 | 0.1 | 0 | 0.26667 | 0.2 | 0.4 | 0 | 0 | 67 | 0.016667 | 0 | 0.022222 | 0.016667 | 0.033333 | 0 | 0
Mechanical ventilation | DE-4 | Window control | Reporting information regarding performance | 0 | 100% | 0 | 0% |  | No reporting | Position of each product & fault detection | Position of each product, fault detection & predictive maintenance | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…) | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…) | 1 |  |  | triage | 1 | 1 | 0 | 0 | 4 | 4 | DE | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 60 | 5% | 5% | 13.33% | 10% | 40% | 5% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DE | 54 | 1 | 0 | 0 | 1 | 0 | 2 | 3 | 0.05 | 0 | 0 | 0.1 | 0 | 0.1 | 0.34286 | 67 | 0.0083333 | 0 | 0 | 0.0083333 | 0 | 0.016667 | 0.028571
| electricity-2 | Feedback - Reporting information | Reporting information regarding energy generation | 2 | 100% | 0 | 0% |  | None | Current generation data available | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 1 |  |  | always | 1 | 1 | 2 | 0 | 4 | 4 | electricity | 24 | 1 | 0 | 0 | 0 | 0 | 1 | 2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.618% | 1.51% | 0% | 10% | 0% | 1.618% | 11.43% | 0.016178 | 0 | 0 | 0 | 0 | 0.016178 | 0.22857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.0026963 | 0 | 0 | 0 | 0 | 0.0026963 | 0.019048 |  | electricity | 26 | 1 | 0 | 0 | 1 | 0 | 2 | 3 | 0.016178 | 0 | 0 | 0.1 | 0 | 0.032355 | 0.34286 | 67 | 0.0026963 | 0 | 0 | 0.0083333 | 0 | 0.0053925 | 0.028571
| electricity-3 | DER - Storage | Storage of locally generated energy | 0 | 100% | 0 | 0% |  | None | Limited: small scale storage (batteries, TES,…) | Storage which can supply self-consumption for > 3 hours | Dynamically operated storage which can also feed back into the grid. |  | 1 |  |  | always | 1 | 1 | 0 | 0 | 3 | 3 | electricity | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.618% | 1.51% | 0% | 10% | 0% | 1.618% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | electricity | 39 | 0 | 3 | 0 | 2 | 0 | 0 | 0 | 0 | 0.045297 | 0 | 0.2 | 0 | 0 | 0 | 67 | 0 | 0.015099 | 0 | 0.016667 | 0 | 0 | 0
| electricity-4 | DER- Optimization | Optimizing self-consumption of locally generated energy | 0 | 100% | 0 | 0% |  | None | short term optimization | long term optimization including predicted generation and/or demand |  |  | 1 |  |  | always | 1 | 1 | 0 | 0 | 2 | 2 | electricity | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.618% | 1.51% | 0% | 10% | 0% | 1.618% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | electricity | 52 | 0 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 0.045297 | 0 | 0 | 0 | 0.032355 | 0 | 67 | 0 | 0.015099 | 0 | 0 | 0 | 0.0053925 | 0
| electricity-5 | DER - Generation Control | CHP control |  | 100% | 0 | 0% |  | Uncontrolled generation depending on the fluctuating availability of RES and or run time of CHP; overproduction will be fed into the grid | Coordination of local RES and CHP with regard to local energy demand profile including energy storage management; Optimization of own consumption |  |  |  | 0 |  |  | triage | 1 | 0 | 0 | 0 | 1 | 0 | electricity | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.618% | 1.51% | 0% | 10% | 0% | 1.618% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | electricity | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| electricity-11 | Feedback - Reporting information | Reporting information regarding stored electricity |  | 100% | 0 | 0% |  | None | Current state of charge (SOC) data available | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | 0 |  |  | triage | 1 | 0 | 0 | 0 | 4 | 0 | electricity | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 59 | 1.618% | 1.51% | 0% | 10% | 0% | 1.618% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | electricity | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting | EV-15 | EV Charging | EV Charging Capacity | 2 | 100% | 0 | 0% |  | Not present | Low charging capacity | Medium charging capacity | High charging capacity |  | 1 |  |  | always | 1 | 1 | 2 | 0 | 3 | 3 | EV | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 61 | 0% | 5% | 0% | 10% | 0% | 0% | 11.43% | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0.0083333 | 0 | 0 | 0 |  | EV | 181 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 0
| EV-16 | EV Charging - Grid | EV Charging Grid balancing | 1 | 100% | 0 | 0% |  | Not present | 1 way (controlled charging) | 2 way (also EV to grid) |  |  | 1 |  |  | triage | 1 | 1 | 1 | 0 | 2 | 2 | EV | 193 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 192 | 0 | -2 | 0 | 0 | 0 | 0 | 0 | Weightings | 61 | 0% | 5% | 0% | 10% | 0% | 0% | 11.43% | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0.016667 | 0 | 0.0083333 | 0 | 0 | 0 |  | EV | 194 | 0 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0.1 | 0 | 0 | 0 | 67 | 0 | 0.05 | 0 | 0.0083333 | 0 | 0 | 0
Lighting | EV-17 | EV Charging - connectivity | EV charging information and connectivity | 0 | 100% | 0 | 0% |  | No information available | Reporting information on EV charging status to occupant | Communication with a back-office compliant to ISO 15118 |  |  | 1 |  |  | triage | 1 | 1 | 0 | 0 | 2 | 2 | EV | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 61 | 0% | 5% | 0% | 10% | 0% | 0% | 11.43% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EV | 208 | 0 | 1 | 0 | 1 | 0 | 0 | 3 | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.34286 | 67 | 0 | 0.016667 | 0 | 0.0083333 | 0 | 0 | 0.028571
| MC-3 | HVAC interaction control | Run time management of HVAC systems | 2 | 100% | 0 | 0% |  | Manual setting (plant enabling) | Individual setting following a predefined time schedule including fixed preconditioning phases | Individual setting following a predefined time schedule; adaptation from a central room; variable preconditioning phases | Control of run time management by artificial intelligence |  | 1 |  |  | always | 1 | 1 | 2 | 0 | 3 | 3 | MC | 38 | 2 | 1 | 2 | 2 | 1 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0.4 | 0.2 | 0.4 | 0.4 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.066667 | 0.066667 | 0.033333 | 0.033333 | 0.016667 | 0 | 0 |  | MC | 39 | 3 | 1 | 2 | 3 | 1 | 0 | 1 | 0.6 | 0.2 | 0.4 | 0.6 | 0.2 | 0 | 0.2 | 67 | 0.1 | 0.066667 | 0.033333 | 0.05 | 0.016667 | 0 | 0.016667
Dynamic building envelope | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | 1 | 100% | 0 | 0% |  | No central indication of detected faults and alarms | With central indication of detected faults and alarms | With central indication of detected faults and alarms / diagnosing functions |  |  | 1 |  |  | always | 1 | 1 | 1 | 0 | 2 | 2 | MC | 51 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0.033333 | 0.033333 | 0.066667 | 0.033333 |  | MC | 52 | 0 | 0 | 0 | 2 | 2 | 3 | 2 | 0 | 0 | 0 | 0.4 | 0.4 | 0.6 | 0.4 | 67 | 0 | 0 | 0 | 0.033333 | 0.033333 | 0.1 | 0.033333
| MC-9 | TBS interaction control | Occupancy detection: connected services | 1 | 100% | 0 | 0% |  | None | For individual functions, e.g. lighting | Centralised detection which feeds in to several TBS such as lighting and heating |  |  | 1 |  |  | always | 1 | 1 | 1 | 0 | 2 | 2 | MC | 107 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0.2 | 0 | 0.2 | 0.2 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.033333 | 0 | 0.016667 | 0.016667 | 0 | 0.033333 | 0 |  | MC | 108 | 1 | 0 | 1 | 1 | 0 | 2 | 0 | 0.2 | 0 | 0.2 | 0.2 | 0 | 0.4 | 0 | 67 | 0.033333 | 0 | 0.016667 | 0.016667 | 0 | 0.066667 | 0
| MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | 3 | 100% | 0 | 0% |  | None | Real time indication of energy use per energy carrier | Real time indication of sub-metererd energy use or other performance metrics for at least 2 domains | Real time indication of sub-metererd energy use or other performance metrics for all main TBS |  | 1 |  |  | always | 1 | 1 | 3 | 0 | 3 | 3 | MC | 165 | 1 | 0 | 0 | 2 | 0 | 1 | 3 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0.2 | 0 | 0 | 0.4 | 0 | 0.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0.033333 | 0 | 0 | 0.033333 | 0 | 0.033333 | 0.05 |  | MC | 165 | 1 | 0 | 0 | 2 | 0 | 1 | 3 | 0.2 | 0 | 0 | 0.4 | 0 | 0.2 | 0.6 | 67 | 0.033333 | 0 | 0 | 0.033333 | 0 | 0.033333 | 0.05
| MC-25 | Smart Grid Integration | Smart Grid Integration | 0 | 100% | 0 | 0% |  | None - No harmonization between grid and building energy systems; building is operated independently from the grid load | Building energy systems are managed and operated depending on grid load; demand side management is used for load shifting |  |  |  | 1 |  |  | always | 1 | 1 | 0 | 0 | 1 | 1 | MC | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MC | 331 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0
Energy generation | MC-28 | Feedback - Reporting information | Reporting information regarding DSM | 0 | 100% | 0 | 0% |  | None | Reporting information on current DSM flows and controls | Reporting information on current, historical and predicted DSM flows and controls |  |  | 1 |  |  | always | 1 | 1 | 0 | 0 | 2 | 2 | MC | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MC | 374 | 0 | 1 | 0 | 0 | 0 | 1 | 3 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.6 | 67 | 0 | 0.066667 | 0 | 0 | 0 | 0.033333 | 0.05
| MC-29 | Override control | Override of DSM control | 0 | 100% | 0 | 0% |  | No DSM control | DSM control without the possibility to override this control by the occupant | Manual override and reactivation | Scheduled override of DSM control and reactivation | Scheduled override of DSM control and reactivation with artificial intelligence | 1 |  |  | always | 1 | 1 | 0 | 0 | 4 | 4 | MC | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Weightings | 62 | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MC | 390 | 0 | 2 | 0 | 3 | 0 | 2 | 2 | 0 | 0.4 | 0 | 0.6 | 0 | 0.4 | 0.4 | 67 | 0 | 0.13333 | 0 | 0.05 | 0 | 0.066667 | 0.033333

## Results
Smart Readiness Indicator for Buildings
Please note that the presentation of results does not reflect the final intended presentation/format of the SRI, but is merely provided for testing purposes.
Research on the proper format is ongoing.
TOTAL SRI SCORE | 67.23%
IMPACT SCORES
Energy savings on site | 78.65%
Flexibility for the grid and storage | 50.96%
Comfort | 77.53%
Convenience | 61.43%
Wellbeing and health | 82.61%
Maintenance & fault prediction | 54.8%
information to occupants | 47.88%
DOMAIN SCORES
Heating system | 81.21%
Domestic Hot Water | 43.15%
Cooling system | 90.22%
Controlled ventilation | 87.08%
Lighting | 68.18%
Dynamic Envelope | 0%
Electricity: renewables & storage | 25.13%
Electric Vehicle Charging | 25.93%
Monitoring & Control | 45.24%

## Weightings
USER DEFINED
user-defined
DOMAIN WEIGHTINGS
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
Heating system | 11.11% | 12.5% | 16.67% | 11.11% | 0% | 14.29% | 12.5%
Domestic Hot Water | 11.11% | 12.5% | 16.67% | 11.11% | 0% | 14.29% | 12.5%
Cooling system | 11.11% | 12.5% | 16.67% | 11.11% | 0% | 14.29% | 12.5%
Controlled ventilation | 11.11% | 12.5% | 16.67% | 11.11% | 50% | 14.29% | 12.5%
Lighting | 11.11% | 0% | 16.67% | 11.11% | 0% | 0% | 0%
Electricity: renewables & storage | 11.11% | 12.5% | 0% | 11.11% | 0% | 14.29% | 12.5%
Dynamic Envelope | 11.11% | 12.5% | 16.67% | 11.11% | 50% | 14.29% | 12.5%
Electric Vehicle Charging | 11.11% | 12.5% | 0% | 11.11% | 0% | 0% | 12.5%
Monitoring & Control | 11.11% | 12.5% | 0% | 11.11% | 0% | 14.29% | 12.5%
| 100% | 100% | 100% | 100% | 100% | 100% | 100%
IMPACT WEIGHTINGS
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| 14.29% | 14.29% | 14.29% | 14.29% | 14.29% | 14.29% | 14.29% | 100%
NOTE: some cells are set to zero and cannot be changed. This means that for these domains, the services have no impact on the given impact criterion.
=> no weight should be attributed.
DEFAULT
residential
DOMAIN WEIGHTINGS
northern europe | [8 empty] | western europe | [8 empty] | southern europe | [8 empty] | north-eastern europe | [8 empty] | south-eastern europe
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
Heating system | 0.30104 | 0.28097 | 0.13333 | 0.1 | 0 | 0.30104 | 0.11429 |  | Heating system | 0.35302 | 0.32949 | 0.13333 | 0.1 | 0 | 0.35302 | 0.11429 |  | Heating system | 0.3209 | 0.29951 | 0.13333 | 0.1 | 0 | 0.3209 | 0.11429 |  | Heating system | 0.3059 | 0.28551 | 0.13333 | 0.1 | 0 | 0.3059 | 0.11429 |  | Heating system | 0.21477 | 0.20045 | 0.13333 | 0.1 | 0 | 0.21477 | 0.11429
Domestic Hot Water | 0.093362 | 0.087138 | 0.13333 | 0.1 | 0 | 0.093362 | 0.11429 |  | Domestic Hot Water | 0.070797 | 0.066077 | 0.13333 | 0.1 | 0 | 0.070797 | 0.11429 |  | Domestic Hot Water | 0.1004 | 0.093704 | 0.13333 | 0.1 | 0 | 0.1004 | 0.11429 |  | Domestic Hot Water | 0.14109 | 0.13168 | 0.13333 | 0.1 | 0 | 0.14109 | 0.11429 |  | Domestic Hot Water | 0.060675 | 0.05663 | 0.13333 | 0.1 | 0 | 0.060675 | 0.11429
Cooling system | 0 | 0 | 0.13333 | 0.1 | 0 | 0 | 0.11429 |  | Cooling system | 0.015305 | 0.014285 | 0.13333 | 0.1 | 0 | 0.015305 | 0.11429 |  | Cooling system | 0.069645 | 0.065002 | 0.13333 | 0.1 | 0 | 0.069645 | 0.11429 |  | Cooling system | 0 | 0 | 0.13333 | 0.1 | 0 | 0 | 0.11429 |  | Cooling system | 0.1524 | 0.14224 | 0.13333 | 0.1 | 0 | 0.1524 | 0.11429
Controlled ventilation | 0.18858 | 0.17601 | 0.13333 | 0.1 | 0.4 | 0.18858 | 0.11429 |  | Controlled ventilation | 0.18518 | 0.17283 | 0.13333 | 0.1 | 0.4 | 0.18518 | 0.11429 |  | Controlled ventilation | 0.093182 | 0.08697 | 0.13333 | 0.1 | 0.4 | 0.093182 | 0.11429 |  | Controlled ventilation | 0.19163 | 0.17886 | 0.13333 | 0.1 | 0.4 | 0.19163 | 0.11429 |  | Controlled ventilation | 0.11266 | 0.10515 | 0.13333 | 0.1 | 0.4 | 0.11266 | 0.11429
Lighting | 0.03725 | 0.034766 | 0.13333 | 0.1 | 0 | 0.03725 | 0 |  | Lighting | 0.014268 | 0.013316 | 0.13333 | 0.1 | 0 | 0.014268 | 0 |  | Lighting | 0.026994 | 0.025194 | 0.13333 | 0.1 | 0 | 0.026994 | 0 |  | Lighting | 0.0062886 | 0.0058694 | 0.13333 | 0.1 | 0 | 0.0062886 | 0 |  | Lighting | 0.0093697 | 0.0087451 | 0.13333 | 0.1 | 0 | 0.0093697 | 0
Electricity: renewables & storage | 0.12977 | 0.12112 | 0 | 0.1 | 0 | 0.12977 | 0.11429 |  | Electricity: renewables & storage | 0.11143 | 0.104 | 0 | 0.1 | 0 | 0.11143 | 0.11429 |  | Electricity: renewables & storage | 0.13888 | 0.12962 | 0 | 0.1 | 0 | 0.13888 | 0.11429 |  | Electricity: renewables & storage | 0.10508 | 0.098079 | 0 | 0.1 | 0 | 0.10508 | 0.11429 |  | Electricity: renewables & storage | 0.20013 | 0.18679 | 0 | 0.1 | 0 | 0.20013 | 0.11429
Dynamic Envelope | 0.05 | 0.05 | 0.13333 | 0.1 | 0.4 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0.05 | 0.13333 | 0.1 | 0.4 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0.05 | 0.13333 | 0.1 | 0.4 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0.05 | 0.13333 | 0.1 | 0.4 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0.05 | 0.13333 | 0.1 | 0.4 | 0.05 | 0.11429
Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429
Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1
non-residential
DOMAIN WEIGHTINGS
northern europe | [8 empty] | western europe | [8 empty] | southern europe | [8 empty] | north-eastern europe | [8 empty] | south-eastern europe
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
Heating system | 0.31063 | 0.28992 | 0.13333 | 0.1 | 0 | 0.31063 | 0.11429 |  | Heating system | 0.27887 | 0.26027 | 0.13333 | 0.1 | 0 | 0.27887 | 0.11429 |  | Heating system | 0.31109 | 0.29035 | 0.13333 | 0.1 | 0 | 0.31109 | 0.11429 |  | Heating system | 0.30026 | 0.28024 | 0.13333 | 0.1 | 0 | 0.30026 | 0.11429 |  | Heating system | 0.29191 | 0.27245 | 0.13333 | 0.1 | 0 | 0.29191 | 0.11429
Domestic Hot Water | 0.05443 | 0.050802 | 0.13333 | 0.1 | 0 | 0.05443 | 0.11429 |  | Domestic Hot Water | 0.078365 | 0.073141 | 0.13333 | 0.1 | 0 | 0.078365 | 0.11429 |  | Domestic Hot Water | 0.10263 | 0.095785 | 0.13333 | 0.1 | 0 | 0.10263 | 0.11429 |  | Domestic Hot Water | 0.091068 | 0.084997 | 0.13333 | 0.1 | 0 | 0.091068 | 0.11429 |  | Domestic Hot Water | 0.1111 | 0.1037 | 0.13333 | 0.1 | 0 | 0.1111 | 0.11429
Cooling system | 0.093403 | 0.087176 | 0.13333 | 0.1 | 0 | 0.093403 | 0.11429 |  | Cooling system | 0.11843 | 0.11054 | 0.13333 | 0.1 | 0 | 0.11843 | 0.11429 |  | Cooling system | 0.11287 | 0.10535 | 0.13333 | 0.1 | 0 | 0.11287 | 0.11429 |  | Cooling system | 0.077449 | 0.072286 | 0.13333 | 0.1 | 0 | 0.077449 | 0.11429 |  | Cooling system | 0.076446 | 0.07135 | 0.13333 | 0.1 | 0 | 0.076446 | 0.11429
Controlled ventilation | 0.19459 | 0.18162 | 0.13333 | 0.1 | 0.4 | 0.19459 | 0.11429 |  | Controlled ventilation | 0.14628 | 0.13653 | 0.13333 | 0.1 | 0.4 | 0.14628 | 0.11429 |  | Controlled ventilation | 0.090333 | 0.084311 | 0.13333 | 0.1 | 0.4 | 0.090333 | 0.11429 |  | Controlled ventilation | 0.18809 | 0.17556 | 0.13333 | 0.1 | 0.4 | 0.18809 | 0.11429 |  | Controlled ventilation | 0.15312 | 0.14291 | 0.13333 | 0.1 | 0.4 | 0.15312 | 0.11429
Lighting | 0.080762 | 0.075378 | 0.13333 | 0.1 | 0 | 0.080762 | 0 |  | Lighting | 0.098294 | 0.091741 | 0.13333 | 0.1 | 0 | 0.098294 | 0 |  | Lighting | 0.11553 | 0.10783 | 0.13333 | 0.1 | 0 | 0.11553 | 0 |  | Lighting | 0.07089 | 0.066164 | 0.13333 | 0.1 | 0 | 0.07089 | 0 |  | Lighting | 0.087248 | 0.081431 | 0.13333 | 0.1 | 0 | 0.087248 | 0
Electricity: renewables & storage | 0.016178 | 0.015099 | 0 | 0.1 | 0 | 0.016178 | 0.11429 |  | Electricity: renewables & storage | 0.029766 | 0.027782 | 0 | 0.1 | 0 | 0.029766 | 0.11429 |  | Electricity: renewables & storage | 0.017545 | 0.016375 | 0 | 0.1 | 0 | 0.017545 | 0.11429 |  | Electricity: renewables & storage | 0.02224 | 0.020758 | 0 | 0.1 | 0 | 0.02224 | 0.11429 |  | Electricity: renewables & storage | 0.030169 | 0.028158 | 0 | 0.1 | 0 | 0.030169 | 0.11429
Dynamic Envelope | 0.05 | 0.05 | 0.13333 | 0.1 | 0.4 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0.05 | 0.13333 | 0.1 | 0.4 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0.05 | 0.13333 | 0.1 | 0.4 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0.05 | 0.13333 | 0.1 | 0.4 | 0.05 | 0.11429 |  | Dynamic Envelope | 0.05 | 0.05 | 0.13333 | 0.1 | 0.4 | 0.05 | 0.11429
Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429 |  | Electric Vehicle Charging | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429
Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | Monitoring & Control | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS | [8 empty] | IMPACT WEIGHTINGS
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants |  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
| 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1 |  | 0.16667 | 0.33333 | 0.083333 | 0.083333 | 0.083333 | 0.16667 | 0.083333 | 1
ORDINAL SCORES
LEGEND
0 | the services within this domain have no contribution to the given impact criterion
1 | at least one service within this domain contributes to the given impact criterion
| Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants
Heating system | 1 | 1 | 1 | 1 | 0 | 1 | 1
Domestic Hot Water | 1 | 1 | 1 | 1 | 0 | 1 | 1
Cooling system | 1 | 1 | 1 | 1 | 0 | 1 | 1
Controlled ventilation | 1 | 1 | 1 | 1 | 1 | 1 | 1
Lighting | 1 | 0 | 1 | 1 | 0 | 0 | 0
Electricity: renewables & storage | 1 | 1 | 0 | 1 | 0 | 1 | 1
Dynamic Envelope | 1 | 1 | 1 | 1 | 1 | 1 | 1
Electric Vehicle Charging | 0 | 1 | 0 | 1 | 0 | 0 | 1
Monitoring & Control | 1 | 1 | 0 | 1 | 0 | 1 | 1
ENERGY BALANCE DATA
RESIDENTIAL |  | North | West | South | North-East | South-East
| Heating | 40.1381 | 47.0695 | 42.7867 | 40.7873 | 28.6358
| DHW | 12.4482 | 9.4395 | 13.3863 | 18.8118 | 8.09
| Cooling | 0 | 2.0407 | 9.286 | 0 | 20.3199
| Ventilation | 25.1443 | 24.6902 | 12.4243 | 25.551 | 15.0208
| Lighting | 4.9666 | 1.9024 | 3.5992 | 0.83849 | 1.2493
| Electricity | 17.3028 | 14.8576 | 18.5176 | 14.0113 | 26.6841
NON RESIDENTIAL |  | North | West | South | North-East | South-East
| Heating | 41.4177 | 37.1821 | 41.4788 | 40.0343 | 38.9215
| DHW | 7.2574 | 10.4486 | 13.6836 | 12.1424 | 14.8138
| Cooling | 12.4538 | 15.7908 | 15.0494 | 10.3266 | 10.1929
| Ventilation | 25.9459 | 19.5038 | 12.0445 | 25.0793 | 20.4162
| Lighting | 10.7683 | 13.1058 | 15.4045 | 9.452 | 11.633
| Electricity | 2.157 | 3.9688 | 2.3393 | 2.9654 | 4.0226

## overview_of_services
Domain | Code | Service group | Smart ready service | Functionality level 0 (as non-smart default) | Functionality level 1 | Functionality level 2 | Functionality level 3 | Functionality level 4 | Standard used | Actionable | part of the proposed simplified indicator | Preconditions / Dependency on other services or building types | Comments | Basis for impacts ascribed to functionality | Usual scale of impact | Degree by which the impact can be ascribed to the functionality | Degree to which the functionality can be determined by inspection | 19
Heating | Heating-1a | Heat control - demand side | Heat emission control | No automatic control | Central automatic control (e.g. central thermostat) | Individual room control (e.g. thermostatic valves, or electronic controller) | Individual room control with communication between controllers and to BACS (e.g. scheduler, room temperature setpoint) | Individual room control with communication and presence control | EN 15232 | 1 | 1 | Always to be assessed, except if TABS is present. | Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High | High - taken directly from EN15232 | High but levels 3 and 4 are harder to assess | heating
Heating | Heating-1b | Heat control - demand side | Emission control for TABS (heating mode) | No automatic control | Central automatic control | Advanced central automatic control | Advanced central automatic control with intermittent operation and/or room temperature feedback control |  | EN 15232 | 1 | 1 | Triage: only relevant in case of TABS. Mostly restricted to non-residential buildings | Level 2 functionality will not be evident from simple inspection, thus some other mechanism will be needed to facilitate assessment. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High | High - taken directly from EN15232 | Medium but level 2 will be hard to assess | heating
Heating | Heating-1c | Heat control - demand side | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks | No automatic control | Outside temperature compensated control | Demand based control |  |  | EN 15232 | 1 | 1 | Not applicable in case of individual heaters (e.g. stoves) | Level 2 functionality will not be evident from simple inspection, thus some other mechanism will be needed to facilitate assessment. For level 1 inspection will suffice. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High | High - taken directly from EN15232 | Medium but level 2 will be hard to assess | heating
Heating | Heating-1d | Heat control - demand side | Control of distribution pumps in networks | No automatic control | On off control | Multi-Stage control | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (external demand signal) | EN 15232 | 1 | 1 | Only applicable for hydronic heating systems | The level of functionality has a big impact on pump energy demand but this is usually a medium-sized load. The inspectability of the nature of the control algorithm would need to be facilitated. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium | High - taken directly from EN15232 | Medium - presence of VSD pumps is evident from inspection but their control algorithms less so | heating
Heating | Heating-1e | Heat control - demand side | Intermittent control of emission and/or distribution - One controller can control different rooms/zones having same occupancy patterns | No automatic control | Automatic control with fixed time program | Automatic control with optimum start/stop | Automatic control with demand evaluation |  | EN 15232 | 1 | 1 | Always to be assessed | The inspectability of the nature of the control algorithm would need to be facilitated for levels 2 and 3. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High | High - taken directly from EN15232 | Low/Medium | heating
Heating | Heating-1f | Heat control - demand side | Thermal Energy Storage (TES) for building heating (excluding TABS) | Continuous storage operation | Time-scheduled storage operation | Load prediction based storage operation |  |  |  | 1 | 1 | Only applicable in case thermal energy storage is present. | Note this is service 1.10 in EN15232-1-2017. The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 and 2. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High | High - taken directly from EN15232 | Low/Medium | heating
Heating | Heating-1g | Heat control - demand side | Building preheating control | No automatic control | Program heating schedule in advance | Thermostat self-learning user behavior (presence, setpoint) |  |  |  | 1 | 1 | Always to be assessed | This sub-service could be deleted as it is not in EN15232 and its service seems to be largely covered by other sub-services which are, notably: optimum/stop start and Automatic control with demand evaluation in Heating 1e/Individual room control with communication and presence control in Heating 1a | None | NA | NA | Low | heating
Heating | Heating-2a | Control heat production facilities | Heat generator control (all except heat pumps) | Constant temperature control | Variable temperature control depending on outdoor temperature | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) |  |  | EN 15232 | 1 | 1 | Only applicable in case of combustion heater or district heating | The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 and 2. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High/Medium | High - taken directly from EN15232 | Low | heating
Heating | Heating-2b | Control heat production facilities | Heat generator control (for heat pumps) | On/Off-control of heat generator | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) |  |  | EN 15233 | 1 | 1 | Only applicable in case of heat pumps | The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 and 2; however, inverter capability of HPs is usually clearly indicated in the product literature. Note EN15232-1-2017 has added another sub-service for the outdoor unit which is not included here. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High/Medium | High - taken directly from EN15232 | Medium | heating
Heating | Heating-2c | Control heat production facilities | Heat system control according to external signal (e.g. electricity tariff, gas pricing, load shedding signal etc.) | No automatic control based on external signals | Heat system control according to external signals (tariff, availability of renewables, etc.) | Heat system control according to external signals combined with internal signals (predicted demand, temperature etc.) |  |  |  | ? | 1 |  | This capability is not defined in any standards. The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 and 2. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | None | NA | NA | Low | heating
Heating | Heating-2d | Control heat production facilities | Sequencing of different heat generators | Priorities only based on running time | Control according to fixed priority list: e.g. heat pump prior to hot water boiler | Control according to dynamic priority list (based on current efficiency and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | Control according to dynamic priority list (based on current AND predicted load, efficiency and capacity of generators) | Control according to dynamic priority list (based on current AND predicted load, efficiency, capacity of generators AND external signals from grid) | EN 15232 + expanded | 1 | 1 | Only applicable in case of multiple heat generators, mostly restricted to large buildings | The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 to 3. Note a) this service has been updated here to match the functional definitions in EN15232-1-2017 which are amended from the earlier version. Note b), this capability is only relevant when different generators are present. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High | High - taken directly from EN15232 | Low | heating
Heating | Heating-2e | Control heat production facilities | Control of on-site waste heat recovery fed into the heating system (e.g. excess heat from data centers) | No heat recovery control | Heat recovery on/off control based on availability | Variable control of waste heat recovery (modulating power based on needs and waste heat availability) | Variable control of waste heat recovery with possibility to store excess heat or time shift heat recovery |  | No standards available | 0 | 0 | Only applicable in case of large waste heat. | This service is amended from Task 1 to be aligned with EN15232-1-2017 (service 7.6). Classifying managed waste heat use/heat shifting is likely to require facilitation. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High/Medium | Medium - taken directly from EN15232 | Medium | heating
Heating | Heating-3 | Information to occupants and facility managers | Report information regarding HEATING system performance | None | Indication of actual values (e.g. temperatures, submetering energy usage) | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | No standards available | 1 | 1 | [6 empty] | heating
Heating | Heating-4 | DSM control of equipment | DSM control of equipment | Not present | Heating system subject to Demand Side Management |  |  |  | None | ? | 0 | The inspectability of the nature of the control algorithm would need to be facilitated | The inspectability of the nature of the control algorithm would need to be facilitated | None | Medium/High | Medium | Medium | heating
Domestic hot water | DHW-1a | Control DHW production facilities | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) | Automatic control on / off | Automatic control on / off and scheduled charging enable | Automatic control on / off and scheduled charging enable and multi-sensor storage management | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) |  | EN 15232, except level 3 | 1 | 1 | Only applicable in case of DHW storage with electric heating | The wording re the functionality is slightly amended to be aligned with EN15232-1-2017 (service 2.1). The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 and 2. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium | High - taken directly from EN15232 | Low | dhw
Domestic hot water | DHW-1b | Control DHW production facilities | Control of DHW storage charging (using hot water generation) | Automatic control on / off | Automatic control on / off and scheduled charging enable | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | Automatic charging control based on signals from district heating grid (DR, DSM) |  | EN 15232, except level 3 | 1 | 1 | Only applicable in case of DHW storage with non-electrical heat generation | The wording re the functionality and the number of functional levels is amended from previous versions to be aligned with EN15232-1-2017 (service 2.2). The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 and 2. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium | High - taken directly from EN15232 | Low | dhw
Domestic hot water | DHW-1c | Control DHW production facilities | Control of DHW storage temperature, varying seasonally: with heat generation or integrated electric heating | Manual selected control with charging pump on / off or electric heating | Automatic selected control with charging pump on / off or electric heating and charging time release | Automatic selected control with charging pump on / off or electric heating, charging time release and demand-oriented supply or multi-sensor storage management | Automatic selected control with heat generation, demand-oriented supply and return temperature control or electric heating, charging time release and multi-sensor storage management |  | EN 15232 | 1 | 0 |  | This capability is no longer within EN15232 (version-1-17). | Building energy simulation for EN15232 | Medium | High - taken directly from EN15232:2012 | Low
Domestic hot water | DHW-1d | Control DHW production facilities | Control of DHW storage charging (with solar collector and supplymentary heat generation) | Manual selected control of solar energy or heat generation | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management |  | EN 15232 | 1 | 1 | Only applicable in case of DHW storage with solar collector | The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 to 3. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium/High | High - taken directly from EN15232 | Low | dhw
Domestic hot water | DHW-2 | DHW control - demand side | Control of DHW circulation pump | No control | Control with time switch program | Demand-oriented control |  |  | EN 15232 | 1 | 0 | Only applicable in case of DHW circulation pump | The wording re the functionality and the number of functional levels is amended from Task 1 to be aligned with EN15232-1-2017 (service 2.4). Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Low | High - taken directly from EN15232 | High/Medium
Domestic hot water | DHW-3 | Information to occupants and facility managers | Report information regarding domestic hot water performance | None | Indication of actual values (e.g. temperatures, submetering energy usage) | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | No standards available | 1 | 1 | [6 empty] | dhw
Domestic hot water | DHW-4 | DSM control of equipment | DSM control of equipment | Not present | Domestic Hot Water production subject to Demand Side Management |  |  |  | None | ? | 0 | The inspectability of the nature of the control algorithm would need to be facilitated | The inspectability of the nature of the control algorithm would need to be facilitated | None | Medium/High | Medium | Medium | dhw
Cooling | Cooling-1a | Cooling control - demand side | Cooling emission control | No automatic control | Central automatic control | Individual room control REF | Individual room control with communication between controllers and to BACS | Individual room control with communication and presence control | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems are present | EN15232-1-2017 (service 2.1). The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 and 2. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High when cooling is significant | High - taken directly from EN15232 | High but levels 3 and 4 are harder to assess | cooling
Cooling | Cooling-1b | Cooling control - demand side | Emission control for TABS (cooling mode) | No automatic control | Central automatic control | Advanced central automatic control | Advanced central automatic control with intermittent operation and/or room temperature feedback control |  | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems based on TABS are present | Functionality will not be evident from simple inspection, thus some other mechanism will be needed to facilitate assessment. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High when cooling is significant | High - taken directly from EN15232 | Low | cooling
Cooling | Cooling-1c | Cooling control - demand side | Control of distribution network chilled water temperature (supply or return) | Constant temperature control | Outside temperature compensated control | Demand based control |  |  | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems with hydronic distribution system are present | Level 2 functionality will not be evident from simple inspection, thus some other mechanism will be needed to facilitate assessment. For level 1 inspection will suffice. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High when cooling is significant | High - taken directly from EN15232 | Medium but level 2 will be hard to assess | cooling
Cooling | Cooling-1d | Cooling control - demand side | Control of distribution pumps in networks | No automatic control | On off control | Multi-Stage control | Variable speed pump control (pump unit (internal) estimations) | Variable speed pump control (external demand signal) | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems with hydronic distribution system are present | The level of functionality has a big impact on pump energy demand but this is usually a medium-sized load. The inspectability of the nature of the control algorithm would need to be facilitated. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium | High - taken directly from EN15232 | Medium - presence of VSD pumps is evident from inspection but their control algorithms less so | cooling
Cooling | Cooling-1e | Cooling control - demand side | Intermittent control of emission and/or distribution | No automatic control | Automatic control with fixed time program | Automatic control with optimum start/stop | Automatic control with demand evaluation |  | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems are present | The inspectability of the nature of the control algorithm would need to be facilitated for levels 2 and 3. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High when cooling is significant | High - taken directly from EN15232 | Low/Medium | cooling
Cooling | Cooling-1f | Cooling control - demand side | Interlock between heating and cooling control of emission and/or distribution | No interlock | Partial interlock (dependant of the HVAC system) | Total interlock |  |  | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems are present | Interlocks can be visually inspected but are not necessarily simple to do so. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High when cooling is significant | High - taken directly from EN15232 | Medium | cooling
Cooling | Cooling-1g | Cooling control - demand side | Control of Thermal Energy Storage (TES) operation | Continuous storage operation | Time-scheduled storage operation | Load prediction based storage operation |  |  | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems are present ánd include TES systems | Note this is service 3.9 in EN15232-1-2017. The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 and 2. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High when cooling is significant | High - taken directly from EN15232 | Low/Medium | cooling
Cooling | Cooling-2a | Control cooling production facilities | Generator control for cooling | Constant temperature control | Variable temperature control depending on outdoor temperature | Variable temperature control depending on the load |  |  | EN 15232 | 1 | 1 | Only applicable in case mechanical cooling systems are present | The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 and 2. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High when cooling is significant | High - taken directly from EN15232 | Low | cooling
Cooling | Cooling-2b | Control cooling production facilities | Sequencing of different cooling generators | Priorities only based on running times | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller | Priorities based on generator efficiency and characteristics: the generator operational control is set individually to available generators so that they operate with an overall high degree efficiency | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power |  | EN 15232 | 1 | 1 | Only applicable in case multiple mechanical cooling systems are present | The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 to 3. Note a) this service has been updated here to match the functional definitions in EN15232-1-2017 which are amended from the earlier version. Note b), this capability is only relevant when different generators are present. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High when cooling is significant | High - taken directly from EN15232 | Low | cooling
Cooling | Cooling-3 | Information to occupants and facility managers | Report information regarding cooling system performance | None | Indication of actual values (e.g. temperatures, submetering energy usage) | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | No standards available | 1 | 1 | Only applicable in case mechanical cooling systems are present | [5 empty] | cooling
Cooling | Cooling-4 | DSM control of equipment | DSM control of equipment | Not present | Cooling subject to Demand Side Management |  |  |  | None | ? | 0 | The inspectability of the nature of the control algorithm would need to be facilitated | The inspectability of the nature of the control algorithm would need to be facilitated | None | Medium/High | Medium | Medium | cooling
Controlled ventilation | Ventilation-1a | Air flow control | Supply air flow control at the room level | No ventilation system or manual control | Clock control | Occupancy detection control | Central Demand Control based on air quality sensors (CO2, VOC,...) | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | EN 15232 + expanded | 1 | 1 | Always to be assessed | EN15232-1-2017 (service 4.1). The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 and 2. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium when ventilation is significant | High - taken directly from EN15232 | Medium | ventilation
Controlled ventilation | Ventilation-1b | Air flow control | Adjust the outdoor air flow or exhaust air rate | Fixed OA ratio / OA flow | Staged (low/high) OA ratio / OA flow (time schedule) | Staged (low/high) OA ratio / OA flow (presence) | Variable control |  | EN 15232 | 1 | 1 | Always to be assessed | Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium-Low when ventilation is significant | High - taken directly from EN15232 | Low | ventilation
Controlled ventilation | Ventilation-1c | Air flow control | Air flow or pressure control at the air handler level | No automatic control | On off time control | Multi-stage control | Automatic flow or pressure control (without reset) | Automatic flow or pressure control (with reset) | EN 15232 | 1 | 1 | Only in case of mechanical ventilation | Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium when ventilation is significant | High - taken directly from EN15232 | Low | ventilation
Controlled ventilation | Ventilation-2a | Air temperature control | Room air temp. control (all-air systems) | on-off capacity control | variable capacity control | Demand control |  |  | EN 15232 | 1 | 1 | Only in case of mechanical ventilation with all-air system | Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium when ventilation is significant | High - taken directly from EN15232 | Medium | ventilation
Controlled ventilation | Ventilation-2b | Air temperature control | Room air temp. control (Combined air-water systems) | No coordination | Coordination |  |  |  | EN 15232 | 1 | 0 | Only in case of mechanical ventilation with combined air-water systems | Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium when ventilation is significant | High - taken directly from EN15232 | Medium
Controlled ventilation | Ventilation-2c | Air temperature control | Heat recovery control: prevention of overheating | Without overheating control | Modulate or bypass heat recovery based on sensors in air exhaust | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control |  |  | EN 15232 + expanded | 1 | 1 | Only in case of mechanical ventilation with heat recovery | Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium when ventilation is significant | High - taken directly from EN15232 | Medium/Low | ventilation
Controlled ventilation | Ventilation-2d | Air temperature control | Supply air temperature control | No automatic control | Constant set point | Variable set point with outdoor temperature compensation | Variable set point with load dependant compensation |  | EN 15232 | 1 | 1 | Only in case of mechanical ventilation which supplies heating | Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium when ventilation is significant | High - taken directly from EN15232 | Medium but level 3 will be hard to assess | ventilation
Controlled ventilation | Ventilation-3 | Free cooling | Free cooling with mechanical ventilation system | No automatic control | Night cooling | Free cooling | H,x- directed control |  | EN 15232 | 1 | 1 | Only in case of mechanical or hybrid ventilation | Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium when ventilation is significant | High - taken directly from EN15232 | Low | ventilation
Controlled ventilation | Ventilation-4 | MV system operation | Heat recovery control: icing protection | Without icing protection control: | With icing protection control: |  |  |  | EN 15232 | 1 | 0 | Not part of current version of SRI | Difficult to assess, limited impacts
Controlled ventilation | Ventilation-5 | MV system operation | Humidity control | No automatic control | Dew point control | Direct humidity control |  |  | EN 15232 | 1 | 0 | Not part of current version of SRI | Difficult to assess, limited impacts
Controlled ventilation | Ventilation-6 | Feedback - Reporting information | Reporting information regarding IAQ | None | Air quality sensors (e.g. CO2) and real time autonomous monitoring | Real time monitoring & historical information of IAQ available to occupants | Real time monitoring & historical information of IAQ available to occupants + fault/maintenance detection based on internal sensors | Real time monitoring, historical & predictive information of IAQ (incl. external data e.g. outside temperature, ambient air…) available to occupants + fault/maintenance detection based on internal sensors and historical data | / | ? | 1 | Always to be assessed | [5 empty] | ventilation
Lighting | Lighting-1a | Artificial lighting control | Occupancy control for indoor lighting | Manual on/off switch | Manual on/off switch + additional sweeping extinction signal | Automatic detection (auto on / dimmed or auto off) | Automatic detection (manual on / dimmed or auto off) |  | EN 15232 | 1 | 1 | Always to be assessed | Average impacts derived from multiple simulations to produce BACS factors in EN15232. Note, the standard EN 15193-1: Energy performance requirements for lighting in buildings is more sophisticated than EN15232 but does not include the simplifed BACS factors energy saving assessment that makes the assessment of savings tractable. Having noted this, we believe EN15232 probably underestimates the savings potentials from lighting control. | Building energy simulation for EN15232 | Medium when lighting is significant | High - taken directly from EN15232 | High | lighting
LIghting | Lighting-1b | Artificial lighting control | Mood and time based control of lighting in buildings | Manual on/off | Programmed control | Automated or mobile triggered detection |  |  |  | ? | 0 | ?
Lighting | Lighting-2 | Control artificial lighting power based on daylight levels | Control artificial lighting power based on daylight levels | Manual (central) | Manual (per room / zone) | Automatic switching | Automatic dimming | Scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks) | EN 15232 + expanded | 1 | 1 | Always to be assessed | Average impacts derived from multiple simulations to produce BACS factors in EN15232. Note, the standard EN 15193-1: Energy performance requirements for lighting in buildings is more sophisticated than EN15232 but does not include the simplifed BACS factors energy saving assessment that makes the assessment of savings tractable. Having noted this, we believe EN15232 probably underestimates the savings potentials from lighting control. | Building energy simulation for EN15232 | Medium when lighting is significant | High - taken directly from EN15232 | High | lighting
Dynamic building envelope | DE-1 | Window control | Window solar shading control | No sun shading or only manual operation | Motorized operation with manual control | Motorized operation with automatic control based on sensor data | Combined light/blind/HVAC control | Predictive blind control (e.g. based on weather forecast) | EN 15232 | 1 | 1 | Only applicable in case movable shades, screens or blinds are present | Functionality level 4 has not yet been defined in EN15232-1-17 but has benefits in principle. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | High when cooling is significant and glazing areas high. | High - taken directly from EN15232 | Medium/High | DE
Dynamic building envelope | DE-2 | Window control | Window open/closed control, combined with HVAC system | Manual operation or only fixed windows | Open/closed detection to shut down heating or cooling systems | Level 1 + Automised mechanical window opening based on room sensor data | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling |  | / | ? | 1 |  | Not standardised | no standards available | High | Low - no standards available | High | DE
Dynamic building envelope | DE-3 | Window control | Changing window spectral properties | Individual window control | Automized control | Integrated control with other systems such as heating and lighting |  |  | / | 0 | 0 | Only applicable in case windows with varying spectral properties are available | Not standardised | no standards available | Same order of magnitude as window solar shading control | Low - no standards available | Low
Dynamic building envelope | DE-4 | Feedback - Reporting information | Reporting information regarding performance | No reporting | Position of each product & fault detection | Position of each product, fault detection & predictive maintenance | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…) | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…) | / | 1 | 1 | Only applicable in case movable shades, screens or blinds are present | [5 empty] | DE
Electricity | electricity-1 | DER - Generation Control | Amount of on-site renewable energy generation | None | Limited amount of PV or CHP production | PV or CHP capacity able to cover average needs |  |  | / | ? | 0
Electricity | electricity-2 | Feedback - Reporting information | Reporting information regarding energy generation | None | Current generation data available | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | No standards available | ? | 1 | Only applicable in case of local energy generation | [5 empty] | electricity
Electricity | electricity-3 | DER - Storage | Storage of locally generated energy | None | Limited: small scale storage (batteries, TES,…) | Storage which can supply self-consumption for > 3 hours | Dynamically operated storage which can also feed back into the grid. |  | / | ? | 1 | Only applicable in case of local energy generation | [5 empty] | electricity
Electricity | electricity-4 | DER- Optimization | Optimizing self-consumption of locally generated energy | None | short term optimization | long term optimization including predicted generation and/or demand |  |  | / | ? | 1 | Only applicable in case of local energy generation | [5 empty] | electricity
Electricity | electricity-5 | DER - Generation Control | CHP control | Uncontrolled generation depending on the fluctuating availability of RES and or run time of CHP; overproduction will be fed into the grid | Coordination of local RES and CHP with regard to local energy demand profile including energy storage management; Optimization of own consumption |  |  |  |  | ? | 1 | Only applicable in case of CHP | The inspectability of the nature of the control algorithm would need to be facilitated for level 1. Service 7.3 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium/High | High - taken directly from EN15232 | Medium/High | electricity
Electricity | electricity-6 | DSM- Storage | Services for integration of renewables into the building energy portfolio | None | local control | local optimization based on pricing | grid based optimization | VPP integration |  | ? | 0
Electricity | electricity-7 | DSM- Storage | Services for integrating battery storage systems into energy portfolio | None | local control | local optimization based on pricing | grid based optimization |  |  | ? | 0
Electricity | electricity-8 | DSM- Storage | Support of microgrid operation modes | None | local battery usage | autonmous energy consumption control |  |  |  | ? | 0
Electricity | electricity-9 | DSM- Storage | Integration of smart appliances | None | local control | building based assets optimization | price based optimization | grid based optimization |  | ? | 0
Electricity | electricity-10 | DSM - Local Systems | Flexible start and switch off of home appliances | None | tarif based | grid condition based |  |  |  | ? | 0
Electricity | electricity-11 | Feedback - Reporting information | Reporting information regarding energy storage | None | Current state of charge (SOC) data available | Actual values and historical data | Performance evaluation including forecasting and/or benchmarking | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection |  | ? | 1 | Only applicable in case of local energy storage | [5 empty] | electricity
Electric vehicle charging | EV-1 | EV Charging - non Grid sensors | Charging whenever needed at the charging pole of the building ("dumb charging service") | None | dumb charging | dumb charging for given time | adaptive time charging |  |  | 0 | 0
Electric vehicle charging | EV-3 | EV Charging - Market | Charging with local, building system based control (price signal based charging) | None | dumb charging on single tariff | adaptive tariffs structures with remote access |  |  |  | 0 | 0
Electric vehicle charging | EV-4 | EV Charging - Market | Charging with aggregated control (EV responsible party as VPP balancing responsible party) | None | local optimization | local and grid optimization |  |  |  | 0 | 0
Electric vehicle charging | EV-5 | EV Charging - Market | Charging with aggregated control (EV resposible party under a balance responsible party) | None | local optimization | local and grid optimization |  |  |  | 0 | 0
Electric vehicle charging | EV-7 | EV Charging - non Grid sensors | Grid connected heating for EV in winter time | None | no grid sensor based charging | grid-sensor based charging |  |  |  | 0 | 0
Electric vehicle charging | EV-8 | EV Charging - Grid | Providing system services to DSO operations | None | grid optimized operations | grid and battery lifecycle optimized behaviour |  |  |  | 0 | 0
Electric vehicle charging | EV-9 | EV Charging - non Grid sensors | Charging for optimisation of the EV battery life-cycle | None | car-lifecycle otpmization | car and grid lifecycle optimization |  |  |  | 0 | 0
Electric vehicle charging | EV-10 | EV Charging - Grid | Charging at a commercial building site - roaming | None | charging at non-home pole | charging at public pole | charging in different country and regulatory regime |  |  | 0 | 0
Electric vehicle charging | EV-11 | EV Charging - Market | Charging based on DSO price tags - " local wind storage" | None | storage | storage and feed-in to grid |  |  |  | 0 | 0
Electric vehicle charging | EV-12 | EV Charging - Market and Occupant | Providing the state-of-charge to home display | None | simple webb app car to mobile | integrating the information into BEMS |  |  |  | 0 | 0
Electric vehicle charging | EV-13 | EV Charging - Grid | Fast charging services - mode 4 | None | dumb |  |  |  |  | 0 | 0
Electric vehicle charging | EV-14 | EV Charging - Grid | Vehicle to grid operation and control | None | exists |  |  |  |  | 0 | 0
Electric vehicle charging | EV-15 | EV Charging | EV Charging Capacity | not present | ducting (or simple power plug) available | 0-9% of parking spaces has recharging points | 10-50% or parking spaces has recharging point | >50% of parking spaces has recharging point | No standards available | ? | 1 | Only to be assessed if parking spots available on site | This service is not yet defined in any standard but could be made actionable through fairly straightforward classification. | None | High | High | High | EV
Electric vehicle charging | EV-16 | EV Charging - Grid | EV Charging Grid balancing | Not present | 1 way (controlled charging) | 2 way (also EV to grid) |  |  | No standards available | ? | 1 | Only to be assessed if EV charging available on site | This service is not yet defined in any standard but could be made actionable through fairly straightforward classification. Inspection made need facilitation. | None | High | Medium/High | Medium | EV
Electric vehicle charging | EV-17 | EV Charging - connectivity | EV charging information and connectivity | No information available | Reporting information on EV charging status to occupant | Communication with a back-office compliant to ISO 15118 |  |  |  | 0 | 1 | Only to be assessed if EV charging available on site | [5 empty] | EV
Monitoring and control | MC-1 | HVAC interaction control | Heating and cooling set point management | Manual setting room by room individually | Adaptation from distributed / decentralized plant rooms only | Adaptation from a central room | Adaptation from a central room with frequent set back of user inputs |  | EN 15232 | 1 | 0 |  | The inspectability of the nature of the control algorithm would need to be facilitated for level 3. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium/High | High - taken directly from EN15232 | Medium
Monitoring and control | MC-2 | HVAC interaction control | Control of thermal exchanges | None | Management of heat/cold exchange among zones within one building or among different buildings - present in parts of the building | All occupied area has management of heat/cold exchange among zones within one building or among different buildings |  |  |  | ? | 0 |  | This service is not yet defined in any standard. | None | Medium | Very low | Low
Monitoring and control | MC-3 | HVAC interaction control | Run time management of HVAC systems | Manual setting (plant enabling) | Individual setting following a predefined time schedule including fixed preconditioning phases | Individual setting following a predefined time schedule; adaptation from a central room; variable preconditioning phases | Control of run time management by artificial intelligence |  | EN 15232 + expanded with level 3 | ? | 1 |  | The inspectability of the nature of the control algorithm would need to be facilitated for levels 1 and 2. Service 7.2 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium | High - taken directly from EN15232 | Medium | MC
Monitoring and control | MC-4 | Fault detection | Detecting faults of technical building systems and providing support to the diagnosis of these faults | No central indication of detected faults and alarms | With central indication of detected faults and alarms | With central indication of detected faults and alarms / diagnosing functions |  |  | EN 15232 | 1 | 1 |  | To be clarified: for which systems should this be present? The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.3 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium | High - taken directly from EN15232 | High | MC
Monitoring and control | MC-5 | Feedback - Reporting information | Reporting information regarding current energy consumption | None | Indication of actual values only (e.g. temperatures, meter values) | Trending functions and consumption determination | Analysing, performance evaluation, benchmarking |  | / | ? | 0 |  | Service 7.4 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Building energy simulation for EN15232 | Medium | High - taken directly from EN15232 | High
Monitoring and control | MC-6 | Feedback - Reporting information | Reporting information regarding historical energy consumption | None | Indication of actual values only (e.g. temperatures, meter values) | Trending functions and consumption determination | Analysing, performance evaluation, benchmarking |  | / | ? | 0 |  | This service is not yet defined in any standard. | None | Medium | Low | High
Monitoring and control | MC-7 | Feedback - Reporting information | Reporting information regarding predicted energy consumption | None | Indication of actual values only (e.g. temperatures, meter values) | Trending functions and consumption determination | Analysing, performance evaluation, benchmarking |  | / | ? | 0 |  | This service is not yet defined in any standard. | None | Medium | Low | High
Monitoring and control | MC-9 | TBS interaction control | Occupancy detection: connected services | None | For individual functions, e.g. lighting | Centralised detection which feeds in to several TBS such as lighting and heating |  |  | / | 0 | 1 |  | This service is not yet defined in any standard. | None | Medium | Low | Medium | MC
Monitoring and control | MC-10 | TBS interaction control | Occupancy detection: space and activity | No occupancy detection present | Occupancy detection can determine presence in room | Occupancy detection can determine average number of people in space | Occupancy detection can determine the actual number of people in a space | Occupancy detection can determine position of people in space (e.g. behind desk) | / | 0 | 0 |  | This service is not yet defined in any standard. | None | Medium | Low | Medium
Monitoring and control | MC-11 | Central control of energy consumers | Remote surveillance of building behaviour | Not present | Remote control of main TBS | Remote control of main TBS with centralised occupancy detection | Remote control of main TBS with centralised occupancy detection, automatic non-occupancy default settings and user alerts |  | / | 0 | 0 |  | This service is not yet defined in any standard. | None | Medium | Low | High
Monitoring and control | MC-12 | Central control of energy consumers | Central off-switch for appliances at home | None | simple off switch | off switch with ability for remote operation | secquence of deactivation for load optimisation |  | / | 0 | 0 |  | This service is not yet defined in any standard. | None | Medium | Low | High
Monitoring and control | MC-13 | Feedback - Reporting information | Central reporting of TBS performance and energy use | None | Real time indication of energy use per energy carrier | Real time indication of sub-metererd energy use or other performance metrics for at least 2 domains | Real time indication of sub-metererd energy use or other performance metrics for all main TBS |  | / | ? | 1 | [6 empty] | MC
Monitoring and control | MC-14 | DSM- Grid | Power flows measurement and communications | None | local use of sensor data | use of sensor data in microgrid operations | DSO based use of sensor data |  |  | 0 | 0
Monitoring and control | MC-15 | DSM - Local Systems | Energy delivery KPI tracking and calculation | None | local optimisation |  |  |  |  | 0 | 0
Monitoring and control | MC-16 | DSM- Grid | Fault location and detection | None | local based detection of errors | DSO optimised operations |  |  |  | 0 | 0
Monitoring and control | MC-17 | DSM- Grid | Fault prevention and risk assessment | None | local based detection of errors | DSO optimised operations |  |  |  | 0 | 0
Monitoring and control | MC-18 | DSM- Grid | Fraud detection and losses calculation | None | local based detection of errors | DSO optimised operations |  |  |  | 0 | 0
Monitoring and control | MC-19 | DSM - Local Systems | Neighbourhood energy efficiency calculation | None | local optimization | data exchange for local swarm and optimization | data exchange for local swarm and optimization for DSP vpp control |  |  | 0 | 0
Monitoring and control | MC-20 | DSM- Grid | Demand prediction | None | local optimization | adaptive load forecast |  |  |  | 0 | 0
Monitoring and control | MC-21 | DSM- Grid | Information exchange on renewables generation prediction | None | local optimization | adaptive load forecast |  |  |  | 0 | 0
Monitoring and control | MC-22 | DSM- Storage | Heat management for a multi-tenant house by aggregator | None | occupant best-effort | building best-effort |  |  |  | 0 | 0
Monitoring and control | MC-23 | DSM - Local Systems | DSM control of a device by an aggregator | None | microgrid operations (energy based) | VPP operations (price based) |  |  |  | 0 | 0
Monitoring and control | MC-24 | DSM- Storage | Energy storage penetration prediction | None | local forecast | microgrid based forecast |  |  |  | 0 | 0
Monitoring and control | MC-25 | Smart Grid Integration | Smart Grid Integration | None - No harmonization between grid and building energy systems; building is operated independently from the grid load | Building energy systems are managed and operated depending on grid load; demand side management is used for load shifting |  |  |  | EN15232 | ? | 1 | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | The inspectability of the nature of the control algorithm would need to be facilitated for level 2. Service 7.5 in EN15232-1-17. Average impacts derived from multiple simulations to produce BACS factors in EN15232. | Simulation | Medium/High | Medium | Medium | MC
Monitoring and control | MC-26 | DSM control of equipment | DSM control of equipment | Not present | Smart appliances or DHW subject to DSM control | Heating or cooling subject to DSM control | Heating and cooling subject to DSM control | Smart appliances, DHW, heating and cooling subject to DSM control | None | ? | 0 | The inspectability of the nature of the control algorithm would need to be facilitated | The inspectability of the nature of the control algorithm would need to be facilitated DSM of heating, cooling and DHW integrated in dedicated domains | None | Medium/High | Medium | Medium
Monitoring and control | MC-27 | Connecting PV to DSO grid | Connecting PV to DSO grid | none | simple feed-in | CLS interface | DSO controls |  | / |  | 0
Monitoring and control | MC-28 | Feedback - Reporting information | Reporting information regarding DSM | None | Reporting information on current DSM flows and controls | Reporting information on current, historical and predicted DSM flows and controls |  |  | No standards available | ? | 1 | [6 empty] | MC
Monitoring and control | MC-29 | Override control | Override of DSM control | No DSM control | DSM control without the possibility to override this control by the occupant | Manual override and reactivation | Scheduled override of DSM control and reactivation | Scheduled override of DSM control and reactivation with artificial intelligence | No standards available | ? | 1 | [6 empty] | MC
Various | VA-1 | Coming home - leaving home functions | Coming home - leaving home functions | none | mobile based | RFID based |  |  | / |  | 0
Various | VA-2 | Inactivity recognition services | Inactivity recognition services | none | building based (movement activation) | room based | electricity sensor based (behaviour) |  | / |  | 0
Various | VA-3 | Multi-tenant access control for buildings without keys | Multi-tenant access control for buildings without keys | none | mobile based | RFID based |  |  | / |  | 0
Various | VA-4 | Wellbeing and health | Occupants Wellbeing and health status monitoring services | none | Functionality levels to be defined | Functionality levels to be defined |  |  | / |  | 0
Various | VA-5 | Wellbeing and health | Dementia monitoring | none | Functionality levels to be defined, e.g. Appliance monitoring with alarms | Functionality levels to be defined, e.g. Appliance and person monitoring |  |  | / |  | 0
Various | VA-8 | Rain water Collection | Rain water Collection | none | reducing sewage network prevent overflows | Re-use to prevent waste fo freshwater resources |  |  | / |  | 0
Various | VA-9 | Safety & Alerts | Smoke detection | no smoke detection | smoke detectors | smoke detectors, cross-linked |  |  | / |  | 0
Various | VA-10 | Safety & Alerts | Water leakage detection | no leakage detection | leakage detection | smoke detectors, cross-linked |  |  | / |  | 0
Various | VA-11 | Safety & Alerts | Carbon Monoxide detecion | no CO detection | CO detection | CO detection, cross-linked to other TBS, e.g. warning signals through lighting |  |  | / |  | 0
Various | VA-12 | Safety & Alerts | Emergency notification services | simple alarm | alarm with remote notification |  |  |  | / |  | 0
Various | VA-13 | Safety & Alerts | Smart testing of emergency lighting | No emergency lighting | Emergency lighting with manual testing | Emergency lighting with automatic testing | Emergency lighting with automatic testing, connected to a centralised reporting system |  | / |  | 0
Various | VA-14 | Safety & Alerts | Intelligent alerting on building events | none | basic technology | Artificial Intelligence |  |  | / |  | 0
Various | VA-18 | Cost allocation | Energy Cost Allocation for heating, cooling and water | no energy cost allocation | heat cost allocators (HCA) / meters (M) | HCA / M remote reading walk by | HCA / M remote reading smartphone | HCA / M remote reading continuous information | / |  | 0
Various | VA-19 | Lifts and elevators | Lift and elevator control and dispatching | simple on demand | grouping calls | forecasting |  |  | / |  | 0
Various | VA-20 | Lifts and elevators | Lift and elevator monitoring and maintenance | [7 empty] | 0
Various | VA-21 | Lifts and elevators | Lift and elevator energy revovery | none | present | energy recovery with capacitor or storage |  |  | / |  | 0

## Feedback
Smart Readiness Indicator for Buildings
FEEDBACK FORM
GENERAL |  |  | WEIGHTING FACTORS
Name | Risto Kosonen
Organisation | Aalto U |  | energy | flex | comf | conv | health | maint | info
e-mail address | 0 | HEAT | 0.31063 | 0.28992 | 0.13333 | 0.1 | 0 | 0.31063 | 0.11429
telephone number (optional) | 0 | DHW | 0.05443 | 0.050802 | 0.13333 | 0.1 | 0 | 0.05443 | 0.11429
Building type | non_residential | COOL | 0.093403 | 0.087176 | 0.13333 | 0.1 | 0 | 0.093403 | 0.11429
Building usage | educational | VENT | 0.19459 | 0.18162 | 0.13333 | 0.1 | 0.4 | 0.19459 | 0.11429
Location | Finland | LIGHT | 0.080762 | 0.075378 | 0.13333 | 0.1 | 0 | 0.080762 | 0
climate zone: | North Europe | DE | 0.05 | 0.05 | 0.13333 | 0.1 | 0.4 | 0.05 | 0.11429
Net floor area of the building | 0 | EL | 0.016178 | 0.015099 | 0 | 0.1 | 0 | 0.016178 | 0.11429
Year of construction | 0 | EV | 0 | 0.05 | 0 | 0.1 | 0 | 0 | 0.11429
Building state | 0 | MC | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Preferred weightings | Default
Total SRI score | 67.23%
Below, please provide feedback, specifically for this building. Please use the general feedback survey to provide more general feedback on the methodology.
Is the SRI score in line with initial expectations by the assessor or building owner/user?
Did you do an onsite walkthrough of the building?
How much time did the assessment process take you (excluding travel, administration, intake discussions)?
Which information was missing to complete the assessment?
Are there smart services relevant for this building which are currently not part of the draft SRI methodology?
Were any relevant functionality levels missing for this particular building:
Do you have any indications on the interoperability or cybersecurity of the technical building systems?
For this particular building, you you have any other comments:
ASSESSMENT --> |  |  | ASSESSMENT
|  |  | service | main FL | main share | 2nd FL | 2nd share
|  |  | Heating-1a | 3 | 100% | 0 | 0%
|  |  | Heating-1b | 3 | 90% | 0 | 10%
|  |  | Heating-1c | 2 | 100% | 0 | 0%
|  |  | Heating-1d | 3 | 100% | 0 | 0%
|  |  | Heating-1e | 2 | 100% | 0 | 0%
|  |  | Heating-1f | 0 | 100% | 0 | 0%
|  |  | Heating-1g | 1 | 100% | 0 | 0%
|  |  | Heating-2a | 0 | 100% | 0 | 0%
|  |  | Heating-2b | 3 | 100% | 0 | 0%
|  |  | Heating-2c | 2 | 100% | 0 | 0%
|  |  | Heating-2d | 4 | 100% | 0 | 0%
|  |  | Heating-3 | 3 | 100% | 0 | 0%
|  |  | DHW-1a | 0 | 100% | 0 | 0%
|  |  | DHW-1b | 0 | 100% | 0 | 0%
|  |  | DHW-1d | 0 | 100% | 0 | 0%
|  |  | DHW-3 | 1 | 100% | 0 | 0%
|  |  | Cooling-1a | 4 | 100% | 0 | 0%
|  |  | Cooling-1b | 0 | 100% | 0 | 0%
|  |  | Cooling-1c | 2 | 100% | 0 | 0%
|  |  | Cooling-1d | 4 | 100% | 0 | 0%
|  |  | Cooling-1e | 2 | 100% | 0 | 0%
|  |  | Cooling-1f | 2 | 100% | 0 | 0%
|  |  | Cooling-1g | 1 | 100% | 0 | 0%
|  |  | Cooling-2a | 2 | 100% | 0 | 0%
|  |  | Cooling-2b | 1 | 100% | 0 | 0%
|  |  | Cooling-3 | 3 | 100% | 0 | 0%
|  |  | Ventilation-1a | 3 | 100% | 0 | 0%
|  |  | Ventilation-1b | 3 | 100% | 0 | 0%
|  |  | Ventilation-1c | 3 | 100% | 0 | 0%
|  |  | Ventilation-2a | 0 | 100% | 0 | 0%
|  |  | Ventilation-2c | 2 | 100% | 0 | 0%
|  |  | Ventilation-2d | 0 | 100% | 0 | 0%
|  |  | Ventilation-3 | 2 | 100% | 0 | 0%
|  |  | Ventilation-6 | 1 | 100% | 0 | 0%
|  |  | Lighting-1a | 3 | 100% | 0 | 0%
|  |  | Lighting-2 | 2 | 100% | 0 | 0%
|  |  | DE-1 | 0 | 100% | 0 | 0%
|  |  | DE-2 | 0 | 100% | 0 | 0%
|  |  | DE-4 | 0 | 100% | 0 | 0%
|  |  | electricity-2 | 2 | 100% | 0 | 0%
|  |  | electricity-3 | 0 | 100% | 0 | 0%
|  |  | electricity-4 | 0 | 100% | 0 | 0%
|  |  | electricity-5 | 0 | 100% | 0 | 0%
|  |  | electricity-11 | 0 | 100% | 0 | 0%
|  |  | EV-15 | 2 | 100% | 0 | 0%
|  |  | EV-16 | 1 | 100% | 0 | 0%
|  |  | EV-17 | 0 | 100% | 0 | 0%
|  |  | MC-3 | 2 | 100% | 0 | 0%
|  |  | MC-4 | 1 | 100% | 0 | 0%
|  |  | MC-9 | 1 | 100% | 0 | 0%
|  |  | MC-13 | 3 | 100% | 0 | 0%
|  |  | MC-25 | 0 | 100% | 0 | 0%
|  |  | MC-28 | 0 | 100% | 0 | 0%
|  |  | MC-29 | 0 | 100% | 0 | 0%

## heating
| domain | heating | [11 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1
| code | service
► | Heating-1a | Heat emission control |  | Service group: | Heat control - demand side | [8 empty] | line | 4
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control (e.g. central thermostat) | + | 0 | + | + | 0 | 0 | 0 | commom | commom | 1 | central control unit, e.g. thermostat | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Individual room control (e.g. thermostatic valves, or electronic controller) | ++ | 0 | ++ | ++ | 0 | 0 | 0 | commom | commom | 1 | thermostatic valves, electronic controller | 2 | 0 | 2 | 2 | 0 | 0 | 0
| level 3 | Individual room control with communication between controllers and to BACS (e.g. scheduler, room temperature setpoint) | ++ | 0 | ++ | +++ | 0 | + | 0 | rare | commom | 2 | room control units and communication | 2 | 0 | 2 | 3 | 0 | 1 | 0
| level 4 | Individual room control with communication and presence control | +++ | 0 | ++ | +++ | 0 | + | 0 | rare | commom | 2 | room control units, communication and occupancy sensors | 3 | 0 | 2 | 3 | 0 | 1 | 0
Information sources
|  | Standard? | EN 15232 | [6 empty] | EN 15232 | EN 15232 |  | EN 15232
| code | service
► | Heating-1b | Emission control for TABS (heating mode) |  | Service group: | Heat control - demand side | [8 empty] | line | 18
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | + | 0 | + | + | 0 | 0 | 0 | rare | rare | 1 | outsidee air temperature sensor and supply water temperature sensor | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Advanced central automatic control | + | 0 | + | ++ | 0 | 0 | 0 | rare | rare | 1 | room temperature sensor, supply water valve, changeover heating-cooling, outside air temperature sensor | 1 | 0 | 1 | 2 | 0 | 0 | 0
| level 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | ++ | 0 | ++ | +++ | 0 | + | + | rare | rare | 2 | availability of equipment, room temperature sensor, supply water valve, changeover heating-cooling, outside air temperature sensor | 2 | 0 | 2 | 3 | 0 | 1 | 1
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232 | [6 empty] | EN 15232 | EN 15232 |  | EN 15232
| code | service
► | Heating-1c | Control of distribution fluid temperature (supply or return air flow or water flow) - Similar function can be applied to the control of direct electric heating networks |  | Service group: | Heat control - demand side | [8 empty] | line | 32
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Outside temperature compensated control | + | 0 | + | + | 0 | 0 | 0 | common | common | 1 | control unit, flow temperature measurement and outside temperature measurement | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Demand based control | ++ | 0 | + | ++ | 0 | + | 0 | rare | common | 2 | control unit, flow sensor and communication | 2 | 0 | 1 | 2 | 0 | 1 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232 | [6 empty] | EN 15232 | EN 15232 |  | EN 15232
| code | service
► | Heating-1d | Control of distribution pumps in networks |  | Service group: | Heat control - demand side | [8 empty] | line | 46
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off control | + | 0 | + | 0 | 0 | 0 | 0 | common | common | 1 | pump | 1 | 0 | 1 | 0 | 0 | 0 | 0
| level 2 | Multi-Stage control | ++ | 0 | ++ | 0 | 0 | 0 | 0 | rare | common | 1 | pump with multi-stage, electric/electronic staging device | 2 | 0 | 2 | 0 | 0 | 0 | 0
| level 3 | Variable speed pump control (pump unit (internal) estimations) | +++ | 0 | +++ | 0 | 0 | 0 | 0 | rare | common | 2 | variable speed drive | 3 | 0 | 3 | 0 | 0 | 0 | 0
| level 4 | Variable speed pump control (external demand signal) | +++ | 0 | +++ | 0 | 0 | 0 | 0 | rare | rare | 2 | variable speed drive | 3 | 0 | 3 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232 | [6 empty] | EN 15232 | EN 15232 |  | EN 15232
| code | service
► | Heating-1e | Intermittent control of emission and/or distribution - One controller can control different rooms/zones having same occupancy patterns |  | Service group: | Heat control - demand side | [8 empty] | line | 60
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control with fixed time program | + | 0 | + | + | 0 | 0 | 0 | common | common | 1 | control fixed time program | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Automatic control with optimum start/stop | ++ | 0 | ++ | ++ | 0 | 0 | 0 | rare | common | 1 | time scheduler | 2 | 0 | 2 | 2 | 0 | 0 | 0
| level 3 | Automatic control with demand evaluation | +++ | 0 | +++ | +++ | 0 | 0 | 0 | rare | common | 2 | demand detection (e.g. occupancy sensor, manual occupancy switch) | 3 | 0 | 3 | 3 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | common in non-residential |  | 2 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232 | [6 empty] | EN 15232 | EN 15232 |  | EN 15232
| code | service
► | Heating-1f | Thermal Energy Storage (TES) for building heating (excluding TABS) |  | Service group: | Heat control - demand side | [8 empty] | line | 74
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Continuous storage operation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Time-scheduled storage operation | + | 0 | + | 0 | 0 | 0 | 0 | rare | rare | 1 | - | 1 | 0 | 1 | 0 | 0 | 0 | 0
| level 2 | Load prediction based storage operation | ++ | 0 | + | 0 | 0 | 0 | 0 | rare | rare | 2 | - | 2 | 0 | 1 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232 | [6 empty] | EN 15232 | EN 15232
| code | service
► | Heating-1g | Building preheating control |  | Service group: | Heat control - demand side | [8 empty] | line | 88
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Program heating schedule in advance | + | 0 | + | + | 0 | 0 | + | rare | common | 1 | - | 1 | 0 | 1 | 1 | 0 | 0 | 1
| level 2 | Thermostat self-learning user behavior (presence, setpoint) | ++ | 0 | ++ | ++ | 0 | 0 | + | rare | rare | 2 | - | 2 | 0 | 2 | 2 | 0 | 0 | 1
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Heating-2a | Heat generator control (all except heat pumps) |  | Service group: | Control heat production facilities | [8 empty] | line | 102
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Constant temperature control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Variable temperature control depending on outdoor temperature | + | 0 | + | 0 | 0 | 0 | 0 | common | common | 1 | outdoor temperature sensor, flow temperature sensor | 1 | 0 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable temperature control depending on the load (e.g. depending on supply water temperature set point) | ++ | 0 | ++ | 0 | 0 | 0 | 0 | rare | common | 2 | communication to distribution/heat consumer, flow sensor | 2 | 0 | 2 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232 | [6 empty] | EN 15232 | EN 15232 |  | EN 15232
| code | service
► | Heating-2b | Heat generator control (for heat pumps) |  | Service group: | Control heat production facilities | [8 empty] | line | 116
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | On/Off-control of heat generator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Multi-stage control of heat generator capacity depending on the load or demand (e.g. on/off of several compressors) | + | 0 | + | 0 | 0 | 0 | 0 | rare | rare | 1 | outdoor temperature sensor or communication to external outdoor temperature value | 1 | 0 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable control of heat generator capacity depending on the load or demand (e.g. hot gas bypass, inverter frequency control) | ++ | 0 | ++ | 0 | 0 | 0 | 0 | rare | rare | 2 | communication/transmission of demand | 2 | 0 | 2 | 0 | 0 | 0 | 0
| level 3 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232 | [6 empty] | EN 15232 | EN 15232 |  | EN 15232
| code | service
► | Heating-2c | Heat system control according to external signal (e.g. electricity tariff, gas pricing, load shedding signal etc.) |  | Service group: | Control heat production facilities | [8 empty] | line | 130
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control based on external signals | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Heat system control according to external signals (tariff, availability of renewables, etc.) | + | ++ | 0 | 0 | 0 | 0 | 0 | rare | rare | 3 | external price signals (e.g. from smart meters) | 1 | 2 | 0 | 0 | 0 | 0 | 0
| level 2 | Heat system control according to external signals combined with internal signals (predicted demand, temperature etc.) | ++ | ++ | + | + | 0 | 0 | 0 | rare | rare | 3 | - | 2 | 2 | 1 | 1 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Heating-2d | Sequencing of different heat generators |  | Service group: | Control heat production facilities | [8 empty] | line | 144
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Priorities only based on running time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Control according to fixed priority list: e.g. heat pump prior to hot water boiler | + | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 1 | sequence coordination device with communication/connection to all heat generators | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Control according to dynamic priority list (based on current efficiency and capacity of generators, e.g. solar, geothermal heat, cogeneration plant, fossil fuels) | ++ | 0 | 0 | 0 | 0 | 0 | 0 | rare | rare | 2 | generators with efficiency measurement/output, sequence coordination device with communication/connection to all heat generators | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Control according to dynamic priority list (based on current AND predicted load, efficiency and capacity of generators) | +++ | 0 | 0 | 0 | 0 | 0 | 0 | rare | rare | 3 | sequence coordination device with communication/connection to all heat generators | 3 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Control according to dynamic priority list (based on current AND predicted load, efficiency, capacity of generators AND external signals from grid) | +++ | ++ | 0 | 0 | 0 | 0 | 0 | rare | rare | 3 |  | 3 | 2 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232 | [6 empty] | EN 15232 | EN 15232 |  | EN 15232
| code | service
► | Heating-2e | Control of on-site waste heat recovery fed into the heating system (e.g. excess heat from data centers) |  | Service group: | Control heat production facilities | [8 empty] | line | 158
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No heat recovery control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Heat recovery on/off control based on availability | + | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 1 | - | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Variable control of waste heat recovery (modulating power based on needs and waste heat availability) | ++ | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 2 | - | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Variable control of waste heat recovery with possibility to store excess heat or time shift heat recovery | +++ | ++ | 0 | 0 | 0 | 0 | 0 | rare | rare | 3 | - | 3 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232 | [6 empty] | EN 15232 | EN 15232
| code | service
► | Heating-3 | Report information regarding HEATING system performance |  | Service group: | Information to occupants and facility managers | [8 empty] | line | 172
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Indication of actual values (e.g. temperatures, submetering energy usage) | + | 0 | 0 | 0 | 0 | + | + | common | common | 2 | - | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | + | 0 | 0 | 0 | 0 | + | ++ | rare | rare | 3 | - | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | + | 0 | 0 | 0 | 0 | + | +++ | rare | rare | 5 | - | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | + | 0 | 0 | + | 0 | ++ | +++ | rare | rare | 7 | - | 1 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?
| code | service
| Heating-4 | DSM control of equipment |  | Service group: | DSM control of equipment | [8 empty] | line | 186
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Not present | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Heating system subject to Demand Side Management | 0 | ++ | 0 | 0 | 0 | 0 | 0 | rare | rare | 2 | - | 0 | 2 | 0 | 0 | 0 | 0 | 0
| level 2 | 0 | [10 empty] | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [10 empty] | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## dhw
| domain | domestic hot water | [11 empty] | 1 | 1 | 0 | 1 | 0 | 1 | 1
| code | service
► | DHW-1a | Control of DHW storage charging (with direct electric heating or integrated electric heat pump) |  | Service group: | Control DHW production facilities | [8 empty] | line | 4
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Automatic control on / off | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control on / off and scheduled charging enable | + | + | 0 | + | 0 | 0 | 0 | rare | rare | 1 | Control Equipment with real time clock | 1 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic control on / off and scheduled charging enable and multi-sensor storage management | ++ | + | 0 | ++ | 0 | 0 | 0 | rare | rare | 2 | Multiple sensor for DHW buffer temperature | 2 | 1 | 0 | 2 | 0 | 0 | 0
| level 3 | Automatic charging control based on local availability of renewables or information from electricity grid (DR, DSM) | ++ | ++ | 0 | ++ | 0 | 0 | 0 | rare | rare | 3 | Multiple sensor for DHW buffer temperature | 2 | 2 | 0 | 2 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | DHW-1b | Control of DHW storage charging (using hot water generation) |  | Service group: | Control DHW production facilities | [8 empty] | line | 18
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Automatic control on / off | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control on / off and scheduled charging enable | + | 0 | 0 | + | 0 | 0 | 0 | common | common | 1 | Control Equipment with real time clock | 1 | 0 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic on/off control, scheduled charging enable and demand-based supply temperature control or multi-sensor storage management | ++ | + | 0 | ++ | 0 | 0 | 0 | rare | rare | 2 | Either control equipment with real time clock, or multi sensing buffer | 2 | 1 | 0 | 2 | 0 | 0 | 0
| level 3 | Automatic charging control based on signals from district heating grid (DR, DSM) | ++ | ++ | 0 | ++ | 0 | 0 | 0 | rare | rare | 3 | Control equipment with real time clock, multi sensing buffer, communication/connection to heat generators for demand transmission | 2 | 2 | 0 | 2 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | DHW-1c | Control of DHW storage temperature, varying seasonally: with heat generation or integrated electric heating |  | Service group: | Control DHW production facilities | [8 empty] | line | 32
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Manual selected control with charging pump on / off or electric heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic selected control with charging pump on / off or electric heating and charging time release | + | + | 0 | + | 0 | 0 | 0 | common | common | 3 | Input for season switching condition: e.g. outdoor sensor, yearly time schedule | 1 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic selected control with charging pump on / off or electric heating, charging time release and demand-oriented supply or multi-sensor storage management | ++ | ++ | 0 | ++ | 0 | 0 | 0 | rare | rare | 3 | Control equipment with real time clock and multi sensing buffer, Input for season switching condition, e.g. outdoor sensor, yearly time schedule | 2 | 2 | 0 | 2 | 0 | 0 | 0
| level 3 | Automatic selected control with heat generation, demand-oriented supply and return temperature control or electric heating, charging time release and multi-sensor storage management | +++ | +++ | 0 | ++ | 0 | 0 | 0 | rare | rare | 3 | Control equipment with real time clock and multi sensing buffer, Input for season switching condition, e.g. outdoor sensor, yearly time schedule | 3 | 3 | 0 | 2 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | DHW-1d | Control of DHW storage charging (with solar collector and supplymentary heat generation) |  | Service group: | Control DHW production facilities | [8 empty] | line | 46
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Manual selected control of solar energy or heat generation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge | + | 0 | 0 | + | 0 | 0 | 0 | rare | rare | 1 | Solar charging equipment (pump, panel sensors, return sensor) | 1 | 0 | 0 | 1 | 0 | 0 | 0
| level 2 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge and demand-oriented supply or multi-sensor storage management | ++ | 0 | 0 | ++ | 0 | 0 | 0 | rare | rare | 2 | Solar charging equipment (pump, panel sensors, return sensor); Either control equipment with real time clock OR multi sensing buffer | 2 | 0 | 0 | 2 | 0 | 0 | 0
| level 3 | Automatic control of solar storage charge (Prio. 1) and supplementary storage charge, demand-oriented supply and return temperature control and multi-sensor storage management | +++ | 0 | 0 | ++ | 0 | 0 | 0 | rare | rare | 3 | Solar charging equipment (pump, panel sensors, return sensor); Control equipment with real time clock and multi sensing buffer | 3 | 0 | 0 | 2 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | DHW-2 | Control of DHW circulation pump |  | Service group: | DHW control - demand side | [8 empty] | line | 60
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Control with time switch program | + | 0 | 0 | + | 0 | 0 | 0 | common | common | 1 | scheduling device for pump | 1 | 0 | 0 | 1 | 0 | 0 | 0
| level 2 | Demand-oriented control | ++ | 0 | 0 | ++ | 0 | 0 | 0 | rare | rare | 2 | Demand detection (temperature sensor, electrical switch, flow sensor, pressure sensor) | 2 | 0 | 0 | 2 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | DHW-3 | Report information regarding domestic hot water performance |  | Service group: | Information to occupants and facility managers | [8 empty] | line | 74
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Indication of actual values (e.g. temperatures, submetering energy usage) | + | 0 | 0 | 0 | 0 | + | + | common | common | 2 | - | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | + | 0 | 0 | 0 | 0 | + | ++ | rare | rare | 3 | - | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | + | 0 | 0 | 0 | 0 | + | +++ | rare | rare | 5 | - | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | + | 0 | 0 | + | 0 | ++ | +++ | rare | rare | 7 | - | 1 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?
| code | service
| DHW-4 | DSM control of equipment |  | Service group: | DSM control of equipment | [8 empty] | line | 88
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Not present | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Domestic Hot Water production subject to Demand Side Management | 0 | ++ | 0 | 0 | 0 | 0 | 0 | rare | rare | 2 | - | 0 | 2 | 0 | 0 | 0 | 0 | 0
| level 2 | 0 | [10 empty] | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [10 empty] | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## cooling
| domain | cooling | [11 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1
| code | service
► | Cooling-1a | Cooling emission control |  | Service group: | Cooling control - demand side | [8 empty] | line | 4
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | + | 0 | + | + | 0 | 0 | 0 | rare | common | 1 | central control unit | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Individual room control REF | + | 0 | + | + | 0 | 0 | 0 | rare | common | 1 | thermostatic valves or electronic control units | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 3 | Individual room control with communication between controllers and to BACS | ++ | 0 | ++ | +++ | 0 | + | 0 | rare | common | 2 | room control units and communication | 2 | 0 | 2 | 3 | 0 | 1 | 0
| level 4 | Individual room control with communication and presence control | +++ | 0 | ++ | +++ | 0 | + | 0 | rare | common | 2 | room control units and communication | 3 | 0 | 2 | 3 | 0 | 1 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Cooling-1b | Emission control for TABS (cooling mode) |  | Service group: | Cooling control - demand side | [8 empty] | line | 18
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Central automatic control | + | 0 | + | + | 0 | 0 | 0 | rare | rare | 1 | outside air temperature sensor, supply water temperature sensor | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Advanced central automatic control | + | 0 | + | + | 0 | 0 | 0 | rare | rare | 1 | room temperature sensor, supply water valve, changeover cooling – heating (if), outside air temperature sensor | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 3 | Advanced central automatic control with intermittent operation and/or room temperature feedback control | ++ | 0 | ++ | ++ | 0 | + | + | rare | rare | 2 | Room temperature sensor, supply water valve, changeover cooling – heating (if), outside air temperature sensor. | 2 | 0 | 2 | 2 | 0 | 1 | 1
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Cooling-1c | Control of distribution network chilled water temperature (supply or return) |  | Service group: | Cooling control - demand side | [8 empty] | line | 32
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Constant temperature control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Outside temperature compensated control | + | 0 | + | + | 0 | 0 | 0 | rare | common | 1 | control unit, flow temperature measurement and outside temperature measurement | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Demand based control | ++ | 0 | ++ | ++ | 0 | 0 | 0 | rare | common | 2 | control unit and temperature sensor and communication | 2 | 0 | 2 | 2 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Cooling-1d | Control of distribution pumps in networks |  | Service group: | Cooling control - demand side | [8 empty] | line | 46
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off control | + | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 1 | pump | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Multi-Stage control | ++ | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 2 | Equipment for multi speed (e.g. pump with multi stage, electrical/electronic staging equipment). | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Variable speed pump control (pump unit (internal) estimations) | +++ | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 3 | variable speed drive | 3 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Variable speed pump control (external demand signal) | +++ | 0 | 0 | 0 | 0 | 0 | 0 | rare | rare | 3 | variable speed drive | 3 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Cooling-1e | Intermittent control of emission and/or distribution |  | Service group: | Cooling control - demand side | [8 empty] | line | 60
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automatic control with fixed time program | + | 0 | + | + | 0 | 0 | 0 | rare | common | 1 | fixed time program | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Automatic control with optimum start/stop | ++ | 0 | + | + | 0 | 0 | 0 | rare | common | 2 | time scheduler | 2 | 0 | 1 | 1 | 0 | 0 | 0
| level 3 | Automatic control with demand evaluation | +++ | 0 | + | + | 0 | 0 | 0 | rare | rare | 3 | demand detection (e.g. occupancy sensor, manual occupancy switch etc). | 3 | 0 | 1 | 1 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Cooling-1f | Interlock between heating and cooling control of emission and/or distribution |  | Service group: | Cooling control - demand side | [8 empty] | line | 74
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No interlock | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Partial interlock (dependant of the HVAC system) | ++ | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 1 | Communication/connection between heating control, cooling control and air temperature control | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Total interlock | +++ | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 2 | Communication/connection between heating control, cooling control and air temperature control | 3 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Cooling-1g | Control of Thermal Energy Storage (TES) operation |  | Service group: | Cooling control - demand side | [8 empty] | line | 88
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Continuous storage operation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Time-scheduled storage operation | + | 0 | + | 0 | 0 | 0 | 0 | rare | rare | 1 | - | 1 | 0 | 1 | 0 | 0 | 0 | 0
| level 2 | Load prediction based storage operation | ++ | 0 | + | 0 | 0 | 0 | 0 | rare | rare | 2 | - | 2 | 0 | 1 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Cooling-2a | Generator control for cooling |  | Service group: | Control cooling production facilities | [8 empty] | line | 103
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Constant temperature control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Variable temperature control depending on outdoor temperature | + | 0 | + | 0 | 0 | 0 | 0 | rare | common | 1 | outdoor temperature sensor, flow temperature sensor | 1 | 0 | 1 | 0 | 0 | 0 | 0
| level 2 | Variable temperature control depending on the load | ++ | 0 | ++ | 0 | 0 | 0 | 0 | rare | rare | 2 | Communication to Distribution/cooling consumer, Flow Sensor | 2 | 0 | 2 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Cooling-2b | Sequencing of different cooling generators |  | Service group: | Control cooling production facilities | [8 empty] | line | 117
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Priorities only based on running times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Fixed sequencing based on loads only: e.g. depending on the generators characteristics such as absorption chiller vs. centrifugal chiller | + | + | 0 | 0 | 0 | 0 | 0 | rare | common | 1 | Sequence coordination device with communication/connection to all heat generators | 1 | 1 | 0 | 0 | 0 | 0 | 0
| level 2 | Priorities based on generator efficiency and characteristics: the generator operational control is set individually to available generators so that they operate with an overall high degree efficiency | + | + | 0 | 0 | 0 | 0 | 0 | rare | rare | 2 | Generators with efficiency measurement/output, Sequence coordination device with communication/connection to all cooling generators | 1 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Load prediction based sequencing: the sequence is based on e.g. COP and available power of a device and the predicted required power | + | + | 0 | 0 | 0 | 0 | 0 | rare | rare | 2 | Sequence coordination device with communication/connection to all cooling generators | 1 | 1 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Cooling-3 | Report information regarding cooling system performance |  | Service group: | Information to occupants and facility managers | [8 empty] | line | 131
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Indication of actual values (e.g. temperatures, submetering energy usage) | + | 0 | 0 | 0 | 0 | + | + | common | common | 2 | - | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | + | 0 | 0 | 0 | 0 | + | ++ | rare | rare | 3 | - | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | + | 0 | 0 | 0 | 0 | + | +++ | rare | rare | 5 | - | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | + | 0 | 0 | + | 0 | ++ | +++ | rare | rare | 7 | - | 1 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?
| code | service
| Cooling-4 | DSM control of equipment |  | Service group: | DSM control of equipment | [8 empty] | line | 145
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Not present | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Cooling subject to Demand Side Management | 0 | ++ | 0 | 0 | 0 | 0 | 0 | rare | rare | 2 | - | 0 | 2 | 0 | 0 | 0 | 0 | 0
| level 2 | 0 | [10 empty] | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [10 empty] | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## ventilation
| domain | mechanical ventilation | [11 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1
| code | service
► | Ventilation-1a | Supply air flow control at the room level |  | Service group: | Air flow control | [8 empty] | line | 4
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No ventilation system or manual control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Clock control | + | 0 | + | + | + | 0 | 0 | rare | common | 1 | scheduling for the specific room / zone. | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Occupancy detection control | + | 0 | ++ | ++ | ++ | 0 | 0 | rare | common | 1 | Presence detection (e.g. occupancy sensor, manual occupancy switch etc) | 1 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | Central Demand Control based on air quality sensors (CO2, VOC,...) | ++ | 0 | +++ | +++ | +++ | 0 | 0 | rare | common | 2 | IAQ sensors | 2 | 0 | 3 | 3 | 3 | 0 | 0
| level 4 | Local Demand Control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers | +++ | 0 | +++ | +++ | +++ | 0 | 0 |  |  |  |  | 3 | 0 | 3 | 3 | 3 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Ventilation-1b | Adjust the outdoor air flow or exhaust air rate |  | Service group: | Air flow control | [8 empty] | line | 18
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Fixed OA ratio / OA flow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Staged (low/high) OA ratio / OA flow (time schedule) | + | 0 | + | + | + | 0 | 0 | rare | common | 2 | - | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Staged (low/high) OA ratio / OA flow (presence) | + | 0 | ++ | ++ | ++ | 0 | 0 | rare | common | 2 | - | 1 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | Variable control | ++ | 0 | ++ | ++ | ++ | 0 | 0 | rare | common | 3 | - | 2 | 0 | 2 | 2 | 2 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Ventilation-1c | Air flow or pressure control at the air handler level |  | Service group: | Air flow control | [8 empty] | line | 32
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | On off time control | + | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 2 | scheduling for the specific air handler | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Multi-stage control | ++ | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 2 | Control equipment for multi-step control for the fan(s). | 2 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | Automatic flow or pressure control (without reset) | +++ | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 3 | Equipment for variable fan speed, pressure sensing equipment, demand communication/Connection to rooms/zones | 3 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | Automatic flow or pressure control (with reset) | +++ | 0 | 0 | 0 | 0 | 0 | 0 | rare | common | 3 | Equipment for variable fan speed, pressure sensing equipment, demand communication/Connection to rooms/zones | 3 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Ventilation-2a | Room air temp. control (all-air systems) |  | Service group: | Air temperature control | [8 empty] | line | 47
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | on-off capacity control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | variable capacity control | + | 0 | + | + | + | 0 | 0 | rare | common | 1 | - | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Demand control | ++ | 0 | + | ++ | ++ | 0 | 0 | rare | common | 2 | - | 2 | 0 | 1 | 2 | 2 | 0 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Ventilation-2b | Room air temp. control (Combined air-water systems) |  | Service group: | Air temperature control | [8 empty] | line | 61
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No coordination | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Coordination | + | 0 | + | + | + | 0 | 0 | rare | common | 2 | - | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Ventilation-2c | Heat recovery control: prevention of overheating |  | Service group: | Air temperature control | [8 empty] | line | 75
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Without overheating control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Modulate or bypass heat recovery based on sensors in air exhaust | + | 0 | + | + | + | 0 | 0 | rare | common | 2 | Temperature Sensor for Supply Air | 1 | 0 | 1 | 1 | 1 | 0 | 0
| level 2 | Modulate or bypass heat recovery based on multiple room temperature sensors or predictive control | ++ | 0 | ++ | ++ | ++ | 0 | 0 | rare | common | 2 | Temperature Sensor for Supply Air | 2 | 0 | 2 | 2 | 2 | 0 | 0
| level 3 | 0 | [7 empty] | - |  | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Ventilation-2d | Supply air temperature control |  | Service group: | Air temperature control | [8 empty] | line | 89
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Constant set point | + | 0 | + | + | 0 | 0 | 0 | rare | common | 1 | Room/zone temperature sensor | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Variable set point with outdoor temperature compensation | ++ | 0 | ++ | + | 0 | 0 | 0 | rare | common | 2 | Room/zone temperature sensor; Outside air sensor (or communication to outside air sensor) | 2 | 0 | 2 | 1 | 0 | 0 | 0
| level 3 | Variable set point with load dependant compensation | +++ | 0 | ++ | + | 0 | 0 | 0 | rare | common | 3 | Room/zone temperature sensor; Flow/air quality control; Communication/connection to static heating/cooling | 3 | 0 | 2 | 1 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Ventilation-3 | Free cooling with mechanical ventilation system |  | Service group: | Free cooling | [8 empty] | line | 103
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Night cooling | ++ | 0 | ++ | ++ | + | 0 | 0 | rare | common | 1 | Outside Temperature Sensor (or communication to outside Air sensor), Room/Zone Temperature Sensor | 2 | 0 | 2 | 2 | 1 | 0 | 0
| level 2 | Free cooling | ++ | 0 | ++ | ++ | + | 0 | 0 | rare | common | 2 | Outside temperature sensor (or communication to outside air sensor); Room/zone temperature sensor | 2 | 0 | 2 | 2 | 1 | 0 | 0
| level 3 | H,x- directed control | +++ | 0 | ++ | ++ | + | 0 | 0 | rare | rare | 3 | Humidity Sensor; Humidifier/dehumidifier actuatorsRoom/zone temperature sensor | 3 | 0 | 2 | 2 | 1 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Ventilation-4 | Heat recovery control: icing protection |  | Service group: | MV system operation | [8 empty] | line | 117
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Without icing protection control: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | With icing protection control: | 0 | 0 | 0 | ++ | 0 | ++ | 0 | rare | common | 1 |  | 0 | 0 | 0 | 2 | 0 | 2 | 0
| level 2 | 0 | [7 empty] | rare | common | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | rare | rare | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Ventilation-5 | Humidity control |  | Service group: | MV system operation | [8 empty] | line | 131
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No automatic control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Dew point control | 0 | 0 | ++ | + | + | 0 | 0 | rare | common | 1 |  | 0 | 0 | 2 | 1 | 1 | 0 | 0
| level 2 | Direct humidity control | 0 | 0 | ++ | + | + | 0 | 0 | rare | common | 2 |  | 0 | 0 | 2 | 1 | 1 | 0 | 0
| level 3 | 0 | [7 empty] | rare | rare | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | Ventilation-6 | Reporting information regarding IAQ |  | Service group: | Feedback - Reporting information | [8 empty] | line | 145
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | common | common | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Air quality sensors (e.g. CO2) and real time autonomous monitoring | 0 | 0 | 0 | 0 | 0 | + | + | rare | rare | 2 | - | 0 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Real time monitoring & historical information of IAQ available to occupants | 0 | 0 | 0 | 0 | 0 | + | ++ | rare | rare | 3 | - | 0 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Real time monitoring & historical information of IAQ available to occupants + fault/maintenance detection based on internal sensors | 0 | 0 | 0 | 0 | 0 | + | +++ | rare | rare | 5 | - | 0 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Real time monitoring, historical & predictive information of IAQ (incl. external data e.g. outside temperature, ambient air…) available to occupants + fault/maintenance detection based on internal sensors and historical data | 0 | 0 | 0 | + | 0 | ++ | +++ | rare | rare | 7 | - | 0 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?

## lighting
| domain | lighting | [11 empty] | 1 | 1 | 1 | 1 | 1 | 0 | 0
| code | service
► | Lighting-1a | Occupancy control for indoor lighting |  | Service group: | Artificial lighting control | [8 empty] | line | 4
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Manual on/off switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Manual on/off switch + additional sweeping extinction signal | + | 0 | + | + | 0 | 0 | 0 | rare | common | 1 | Manual switches; Sweep control device with Real time clock | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Automatic detection (auto on / dimmed or auto off) | ++ | 0 | ++ | ++ | 0 | 0 | 0 | rare | common | 5 | light/brightness, occupancy sensor, manual switch | 2 | 0 | 2 | 2 | 0 | 0 | 0
| level 3 | Automatic detection (manual on / dimmed or auto off) | ++ | 0 | ++ | ++ | 0 | 0 | 0 | rare | rare | 5 | light/brightness, occupancy sensor, manual switch | 2 | 0 | 2 | 2 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15232
| code | service
► | Lighting-1b | Mood and time based control of lighting in buildings |  | Service group: | Artificial lighting control | [8 empty] | line | 18
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Manual on/off | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Programmed control | + | 0 | 0 | + | 0 | 0 | 0 | rare | rare | 1 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0
| level 2 | Automated or mobile triggered detection | + | 0 | 0 | ++ | 0 | 0 | 0 | rare | rare | 2 | - | 1 | 0 | 0 | 2 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | Y | Y | 5 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | EN 15193-1 and CEN-TR 16791 | CEN-TR 16791 | EN 12464-1 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791
| code | service
► | Lighting-2 | Control artificial lighting power based on daylight levels |  | Service group: | Control artificial lighting power based on daylight levels | [8 empty] | line | 32
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Manual (central) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Manual (per room / zone) | + | 0 | + | + | 0 | 0 | 0 | rare | common | 1 | Manual switches | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Automatic switching | ++ | 0 | + | + | + | 0 | 0 | rare | common | 5 | Brightness sensor | 2 | 0 | 1 | 1 | 1 | 0 | 0
| level 3 | Automatic dimming | +++ | 0 | ++ | ++ | ++ | 0 | 0 | rare | rare | 5 | Brightness sensor | 3 | 0 | 2 | 2 | 2 | 0 | 0
| level 4 | Scene-based light control (during time intervals, dynamic and adapted lighting scenes are set, for example, in terms of illuminance level, different correlated colour temperature (CCT) and the possibility to change the light distribution within the space according to e. g. design, human needs, visual tasks) | +++ | 0 | +++ | +++ | +++ | 0 | 0 | rare | rare | 5 |  | 3 | 0 | 3 | 3 | 3 | 0 | 0
Information sources
|  | Standard? | EN 15193-1 and CEN-TR 16791 | CEN-TR 16791 | EN 12464-1 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791 | CEN-TR 16791

## DE
| domain | dynamic building envelope | [11 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1
| code | service
► | DE-1 | Window solar shading control |  | Service group: | Window control | [8 empty] | line | 4
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No sun shading or only manual operation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Motorized operation with manual control | + | 0 | + | + | 0 | 0 | 0 | rare | common | 1 | Switches to manually operate blinds; Motorized blinds | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Motorized operation with automatic control based on sensor data | ++ | 0 | + | ++ | + | 0 | 0 | rare | common | 1 | Solar sensor; Communication to solar brightness sensor; Motorized blinds | 2 | 0 | 1 | 2 | 1 | 0 | 0
| level 3 | Combined light/blind/HVAC control | +++ | 0 | ++ | +++ | + | 0 | 0 | rare | common | 2 | light sensor or communication to light sensor; Communication to room temperature control; Communication to lighting control | 3 | 0 | 2 | 3 | 1 | 0 | 0
| level 4 | Predictive blind control (e.g. based on weather forecast) | +++ | 0 | +++ | +++ | + | 0 | 0 | rare | rare | 3 | light sensor or communication to light sensor; Communication to room temperature control; Communication to lighting control | 3 | 0 | 3 | 3 | 1 | 0 | 0
Information sources
Standard?
| code | service
► | DE-2 | Window open/closed control, combined with HVAC system |  | Service group: | Window control | [8 empty] | line | 18
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Manual operation or only fixed windows | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Open/closed detection to shut down heating or cooling systems | ++ | 0 | + | + | 0 | 0 | 0 | rare | common | 1 | - | 2 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | Level 1 + Automised mechanical window opening based on room sensor data | ++ | 0 | ++ | + | + | 0 | 0 | rare | rare | 2 | - | 2 | 0 | 2 | 1 | 1 | 0 | 0
| level 3 | Level 2 + Centralized coordination of operable windows, e.g. to control free natural night cooling | ++ | 0 | ++ | ++ | + | 0 | 0 | rare | rare | 3 | - | 2 | 0 | 2 | 2 | 1 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | DE-3 | Changing window spectral properties |  | Service group: | Window control | [8 empty] | line | 32
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Individual window control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Automized control | + | 0 | 0 | ++ | 0 | 0 | 0 | rare | rare | 3 | - | 1 | 0 | 0 | 2 | 0 | 0 | 0
| level 2 | Integrated control with other systems such as heating and lighting | +++ | 0 | 0 | +++ | 0 | 0 | 0 | rare | rare | 6 | - | 3 | 0 | 0 | 3 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | rare | rare | 3 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| DE-4 | Reporting information regarding performance |  | Service group: | Feedback - Reporting information | [8 empty] | line | 46
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No reporting | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Position of each product & fault detection | + | 0 | 0 | 0 | 0 | + | + |  |  |  | - | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Position of each product, fault detection & predictive maintenance | + | 0 | 0 | 0 | 0 | + | ++ |  |  |  | - | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature…) | + | 0 | 0 | 0 | 0 | + | +++ |  |  |  | - | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Position of each product, fault detection, predictive maintenance, real-time & historical sensor data (wind, lux, temperature…) | + | 0 | 0 | + | 0 | ++ | +++ |  |  |  |  | 1 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?

## electricity
| domain | Energy generation | [11 empty] | 1 | 1 | 0 | 1 | 0 | 1 | 1
| code | service
► | electricity-1 | Amount of on-site renewable energy generation |  | Service group: | DER - Generation Control | [8 empty] | line | 4
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Limited amount of PV or CHP production | 0 | + | 0 | 0 | 0 | 0 | 0 | + | ++ | 2 | - | 0 | 1 | 0 | 0 | 0 | 0 | 0
| level 2 | PV or CHP capacity able to cover average needs | 0 | ++ | 0 | 0 | 0 | 0 | 0 | + | - | 2 | - | 0 | 2 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | electricity-2 | Local energy generation information |  | Service group: | Feedback - Reporting information | [8 empty] | line | 18
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Current generation data available | + | 0 | 0 | 0 | 0 | + | + | 0 | ++ | 1 | - | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | + | 0 | 0 | 0 | 0 | + | ++ | + | ++ | 2 | - | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | + | 0 | 0 | 0 | 0 | + | +++ | 0 | ++ | 3 | - | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | + | 0 | 0 | + | 0 | ++ | +++ | - | - | 4 | - | 1 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
|  | Standard? | IEC 61850-7-420 | IEC 61850-7-420
| code | service
► | electricity-3 | Storage of locally generated energy |  | Service group: | DER - Storage | [8 empty] | line | 32
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Limited: small scale storage (batteries, TES,…) | 0 | + | 0 | + | 0 | 0 | 0 | + | + | 1 | - | 0 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | Storage which can supply self-consumption for > 3 hours | 0 | ++ | 0 | + | 0 | 0 | 0 | 0 | + | 5 | - | 0 | 2 | 0 | 1 | 0 | 0 | 0
| level 3 | Dynamically operated storage which can also feed back into the grid. | 0 | +++ | 0 | ++ | 0 | 0 | 0 | -- | 0 | 7 | - | 0 | 3 | 0 | 2 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | IEC 61850-7-420 | IEC 61850-7-420 |  |  |  | IEC 61850-7-420
| code | service
► | electricity-4 | Optimizing self-consumption of locally generated energy |  | Service group: | DER- Optimization | [8 empty] | line | 46
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | short term optimization | 0 | + | 0 | 0 | 0 | 0 | 0 | 0 | + | 2 | - | 0 | 1 | 0 | 0 | 0 | 0 | 0
| level 2 | long term optimization including predicted generation and/or demand | 0 | +++ | 0 | 0 | 0 | ++ | 0 | -- | -- | 2 | - | 0 | 3 | 0 | 0 | 0 | 2 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | electricity-5 | CHP control |  | Service group: | DER - Generation Control | [8 empty] | line | 60
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Uncontrolled generation depending on the fluctuating availability of RES and or run time of CHP; overproduction will be fed into the grid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Coordination of local RES and CHP with regard to local energy demand profile including energy storage management; Optimization of own consumption | 0 | ++ | 0 | 0 | 0 | 0 | 0 | 0 | + | 2 | - | 0 | 2 | 0 | 0 | 0 | 0 | 0
| level 2 | 0 | [7 empty] | -- | -- | 2 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| electricity-6 | Services for integration of renewables into the building energy portfolio |  | Service group: | DSM- Storage
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | -
| level 1 | local control | + | + | 0 | 0 | 0 | 0 | 0 | + | + | 5 | -
| level 2 | local optimization based on pricing | + | + | 0 | 0 | 0 | 0 | 0 | + | + | 5 | -
| level 3 | grid based optimization | ++ | ++ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | -
| level 4 | VPP integration | ++ | ++ | 0 | 0 | 0 | 0 | 0 | - | - | 20 | -
Information sources
Standard?
| code | service
| electricity-7 | Services for integrating battery storage systems into energy portfolio |  | Service group: | DSM- Storage
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | -
| level 1 | local control | + | + | 0 | 0 | 0 | - | 0 | + | ++ | 5 | -
| level 2 | local optimization based on pricing | ++ | ++ | 0 | 0 | 0 | - | 0 | 0 | + | 10 | -
| level 3 | grid based optimization | ++ | ++ | 0 | 0 | 0 | - | 0 | - | 0 | 20 | -
| level 4 | 0 | [6 empty] | 0 | - | - | - | -
Information sources
|  | Standard? | IEC PC 118 | IEC PC 118
| code | service
| electricity-8 | Support of microgrid operation modes |  | Service group: | DSM- Storage
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | -
| level 1 | local battery usage | 0 | ++ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | -
| level 2 | autonmous energy consumption control | 0 | ++ | 0 | ++ | 0 | 0 | 0 | 0 | 0 | 20 | -
| level 3 | 0 | - | - | - | - | - | - | - | - | - | - | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
|  | Standard? | IEC TC 57 | IEC TC 57 |  |  |  | IEC TC 57 | IEC TC 57
| code | service
| electricity-9 | Integration of smart appliances |  | Service group: | DSM- Storage
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | -
| level 1 | local control | + | 0 | 0 | + | 0 | - | 0 | ++ | + | 5 | -
| level 2 | building based assets optimization | ++ | + | 0 | + | 0 | - | 0 | + | ++ | 8 | -
| level 3 | price based optimization | ++ | + | 0 | + | 0 | - | 0 | 0 | 0 | 10 | -
| level 4 | grid based optimization | + | + | 0 | + | 0 | - | 0 | 0 | 0 | 10 | -
Information sources
|  | Standard? | EEBUS | EEBUS |  |  |  | EEBUS | EEBUS
| code | service
| electricity-10 | Flexible start and switch off of home appliances |  | Service group: | DSM - Local Systems
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | -
| level 1 | tarif based | 0 | ++ | -- | -- | 0 | 0 | 0 | + | 0 | 5 | -
| level 2 | grid condition based | 0 | ++ | -- | -- | 0 | 0 | 0 | -- | - | 5 | -
| level 3 | 0 | - | - | - | - | - | - | - | - | - | - | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
| electricity-11 | Reporting information regarding energy storage |  | Service group: | Feedback - Reporting information | [8 empty] | line | 144
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Current state of charge (SOC) data available | + | 0 | 0 | 0 | 0 | + | + | 0 | ++ | 1 | - | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | Actual values and historical data | + | 0 | 0 | 0 | 0 | + | ++ | + | ++ | 2 | - | 1 | 0 | 0 | 0 | 0 | 1 | 2
| level 3 | Performance evaluation including forecasting and/or benchmarking | + | 0 | 0 | 0 | 0 | + | +++ | 0 | ++ | 3 | - | 1 | 0 | 0 | 0 | 0 | 1 | 3
| level 4 | Performance evaluation including forecasting and/or benchmarking; also including predictive management and fault detection | + | 0 | 0 | + | 0 | ++ | +++ | - | - | 4 | - | 1 | 0 | 0 | 1 | 0 | 2 | 3
Information sources
Standard?

## EV
| domain | Electric vehicle charging | [11 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1
| code | service
► | EV-1 | Charging whenever needed at the charging pole of the building ("dumb charging service") |  | Service group: | EV Charging - non Grid sensors | [8 empty] | line | 4
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | dumb charging | 0 | - | 0 | + | 0 | 0 | 0 | + | ++ | 1 | - | 0 | -1 | 0 | 1 | 0 | 0 | 0
| level 2 | dumb charging for given time | 0 | - | 0 | ++ | 0 | 0 | 0 | + | + | 2 | - | 0 | -1 | 0 | 2 | 0 | 0 | 0
| level 3 | adaptive time charging | 0 | 0 | 0 | ++ | 0 | 0 | 0 | 0 | 0 | 2 | - | 0 | 0 | 0 | 2 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Information sources | [9 empty] | own judgment
Standard?
| code | service
► | EV-3 | Charging with local, building system based control (price signal based charging) |  | Service group: | EV Charging - Market | [8 empty] | line | 19
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | dumb charging on single tariff | 0 | ++ | 0 | -- | 0 | - | 0 | - | - | 2 | - | 0 | 2 | 0 | -2 | 0 | -1 | 0
| level 2 | adaptive tariffs structures with remote access | 0 | ++ | - | -- | 0 | - | 0 | - | - | 2 | - | 0 | 2 | -1 | -2 | 0 | -1 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-4 | Charging with aggregated control (EV responsible party as VPP balancing responsible party) |  | Service group: | EV Charging - Market | [8 empty] | line | 33
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | local optimization | 0 | + | 0 | 0 | 0 | 0 | 0 | - | - | 2 | - | 0 | 1 | 0 | 0 | 0 | 0 | 0
| level 2 | local and grid optimization | 0 | + | 0 | 0 | 0 | 0 | 0 | - | - | 2 | - | 0 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-5 | Charging with aggregated control (EV resposible party under a balance responsible party) |  | Service group: | EV Charging - Market | [8 empty] | line | 47
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | local optimization | 0 | + | 0 | 0 | 0 | 0 | 0 | -- | -- | 2 | - | 0 | 1 | 0 | 0 | 0 | 0 | 0
| level 2 | local and grid optimization | 0 | + | 0 | 0 | 0 | 0 | 0 | -- | -- | 2 | - | 0 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-7 | Grid connected heating for EV in winter time |  | Service group: | EV Charging - non Grid sensors | [8 empty] | line | 62
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | no grid sensor based charging | 0 | + | ++ | ++ | 0 | 0 | 0 | 0 | 0 | 2 | - | 0 | 1 | 2 | 2 | 0 | 0 | 0
| level 2 | grid-sensor based charging | 0 | + | ++ | ++ | 0 | 0 | 0 | 0 | 0 | 2 | - | 0 | 1 | 2 | 2 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-8 | Providing system services to DSO operations |  | Service group: | EV Charging - Grid | [8 empty] | line | 76
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | grid optimized operations | 0 | +++ | 0 | 0 | 0 | 0 | 0 | - | -- | 5 | - | 0 | 3 | 0 | 0 | 0 | 0 | 0
| level 2 | grid and battery lifecycle optimized behaviour | 0 | +++ | 0 | 0 | 0 | 0 | 0 | - | -- | 5 | - | 0 | 3 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-9 | Charging for optimisation of the EV battery life-cycle |  | Service group: | EV Charging - non Grid sensors | [8 empty] | line | 90
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | car-lifecycle otpmization | 0 | + | 0 | 0 | 0 | ++ | 0 | n/a | n/a | n/a | - | 0 | 1 | 0 | 0 | 0 | 2 | 0
| level 2 | car and grid lifecycle optimization | 0 | ++ | 0 | 0 | 0 | + | 0 | n/a | n/a | n/a | - | 0 | 2 | 0 | 0 | 0 | 1 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-10 | Charging at a commercial building site - roaming |  | Service group: | EV Charging - Grid | [8 empty] | line | 104
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | charging at non-home pole | 0 | + | + | + | 0 | 0 | 0 | + | + | 1 | - | 0 | 1 | 1 | 1 | 0 | 0 | 0
| level 2 | charging at public pole | 0 | + | + | + | 0 | 0 | 0 | ++ | ++ | 1 | - | 0 | 1 | 1 | 1 | 0 | 0 | 0
| level 3 | charging in different country and regulatory regime | 0 | + | + | ++ | 0 | 0 | 0 | ++ | ++ | 1 | - | 0 | 1 | 1 | 2 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-11 | Charging based on DSO price tags - " local wind storage" |  | Service group: | EV Charging - Market | [8 empty] | line | 118
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | storage | 0 | ++ | - | - | 0 | 0 | 0 | - | -- | - | - | 0 | 2 | -1 | -1 | 0 | 0 | 0
| level 2 | storage and feed-in to grid | 0 | ++ | - | - | 0 | 0 | 0 | - | -- | - | - | 0 | 2 | -1 | -1 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-12 | Providing the state-of-charge to home display |  | Service group: | EV Charging - Market and Occupant | [8 empty] | line | 132
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | simple webb app car to mobile | 0 | 0 | 0 | + | 0 | 0 | ++ | + | + | 2 | - | 0 | 0 | 0 | 1 | 0 | 0 | 2
| level 2 | integrating the information into BEMS | 0 | 0 | 0 | + | 0 | 0 | +++ | - | - | 2 | - | 0 | 0 | 0 | 1 | 0 | 0 | 3
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-13 | Fast charging services - mode 4 |  | Service group: | EV Charging - Grid | [8 empty] | line | 146
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | dumb | 0 | 0 | ++ | ++ | 0 | 0 | 0 | ++ | ++ | 2 | - | 0 | 0 | 2 | 2 | 0 | 0 | 0
| level 2 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | IEC 15118
| code | service
► | EV-14 | Vehicle to grid operation and control |  | Service group: | EV Charging - Grid | [8 empty] | line | 160
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | exists | + | +++ | 0 | + | 0 | + | 0 | - | - | - | - | 1 | 3 | 0 | 1 | 0 | 1 | 0
| level 2 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-15 | EV Charging Capacity |  | Service group: | EV Charging | [8 empty] | line | 174
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | not present | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | ducting (or simple power plug) available | 0 | 0 | 0 | + | 0 | 0 | 0 | - | - | - | - | 0 | 0 | 0 | 1 | 0 | 0 | 0
| level 2 | 0-9% of parking spaces has recharging points | 0 | 0 | 0 | + | 0 | 0 | 0 | - | - | - | - | 0 | 0 | 0 | 1 | 0 | 0 | 0
| level 3 | 10-50% or parking spaces has recharging point | 0 | 0 | 0 | ++ | 0 | 0 | 0 | - | - | - | - | 0 | 0 | 0 | 2 | 0 | 0 | 0
| level 4 | >50% of parking spaces has recharging point | 0 | 0 | 0 | +++ | 0 | 0 | 0 | - | - | - | - | 0 | 0 | 0 | 3 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-16 | EV Charging Grid balancing |  | Service group: | EV Charging - Grid | [8 empty] | line | 188
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Not present | 0 | -- | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | -2 | 0 | 0 | 0 | 0 | 0
| level 1 | 1 way (controlled charging) | 0 | + | 0 | + | 0 | 0 | 0 | - | - | - | - | 0 | 1 | 0 | 1 | 0 | 0 | 0
| level 2 | 2 way (also EV to grid) | 0 | +++ | 0 | + | 0 | 0 | 0 | - | - | - | - | 0 | 3 | 0 | 1 | 0 | 0 | 0
| level 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | EV-17 | EV charging information and connectivity |  | Service group: | EV Charging - connectivity | [8 empty] | line | 202
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No information available | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Reporting information on EV charging status to occupant | 0 | 0 | 0 | + | 0 | 0 | ++ | - | - | - | - | 0 | 0 | 0 | 1 | 0 | 0 | 2
| level 2 | Communication with a back-office compliant to ISO 15118 | 0 | + | 0 | + | 0 | 0 | +++ | - | - | - | - | 0 | 1 | 0 | 1 | 0 | 0 | 3
| level 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?

## MC
| domain | Monitoring and control | [11 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1
| code | service
► | MC-1 | Heating and cooling set point management |  | Service group: | HVAC interaction control | [8 empty] | line | 4
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Manual setting room by room individually | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Adaptation from distributed / decentralized plant rooms only | + | + | + | + | + | 0 | + | + | ++ | 2 | - | 1 | 1 | 1 | 1 | 1 | 0 | 1
| level 2 | Adaptation from a central room | + | + | + | + | + | 0 | + | + | ++ | 2 | - | 1 | 1 | 1 | 1 | 1 | 0 | 1
| level 3 | Adaptation from a central room with frequent set back of user inputs | ++ | + | + | + | + | - | + | + | ++ | 2 | - | 2 | 1 | 1 | 1 | 1 | -1 | 1
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Information sources | [9 empty] | own judgment
Standard?
| code | service
► | MC-2 | Control of thermal exchanges |  | Service group: | HVAC interaction control | [8 empty] | line | 18
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Management of heat/cold exchange among zones within one building or among different buildings - present in parts of the building | + | 0 | + | 0 | 0 | 0 | 0 | 0 | + | 2 | - | 1 | 0 | 1 | 0 | 0 | 0 | 0
| level 2 | All occupied area has management of heat/cold exchange among zones within one building or among different buildings | ++ | 0 | + | 0 | 0 | 0 | 0 | - | - | 4 | - | 2 | 0 | 1 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | MC-3 | Run time management of HVAC systems |  | Service group: | HVAC interaction control | [8 empty] | line | 32
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Manual setting (plant enabling) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Individual setting following a predefined time schedule including fixed preconditioning phases | + | + | ++ | ++ | + | 0 | 0 | + | ++ | 5 | - | 1 | 1 | 2 | 2 | 1 | 0 | 0
| level 2 | Individual setting following a predefined time schedule; adaptation from a central room; variable preconditioning phases | ++ | + | ++ | ++ | + | 0 | 0 | + | ++ | 5 | - | 2 | 1 | 2 | 2 | 1 | 0 | 0
| level 3 | Control of run time management by artificial intelligence | +++ | + | ++ | +++ | + | 0 | + | - | - | - | - | 3 | 1 | 2 | 3 | 1 | 0 | 1
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | MC-4 | Detecting faults of technical building systems and providing support to the diagnosis of these faults |  | Service group: | Fault detection | [8 empty] | line | 46
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No central indication of detected faults and alarms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | With central indication of detected faults and alarms | 0 | 0 | 0 | ++ | ++ | ++ | ++ | + | ++ | - | - | 0 | 0 | 0 | 2 | 2 | 2 | 2
| level 2 | With central indication of detected faults and alarms / diagnosing functions | 0 | 0 | 0 | ++ | ++ | +++ | ++ | + | + | - | - | 0 | 0 | 0 | 2 | 2 | 3 | 2
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | MC-5 | Reporting information regarding current energy consumption |  | Service group: | Feedback - Reporting information | [8 empty] | line | 60
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Indication of actual values only (e.g. temperatures, meter values) | 0 | 0 | 0 | 0 | 0 | 0 | + | ++ | ++ | 2 | - | 0 | 0 | 0 | 0 | 0 | 0 | 1
| level 2 | Trending functions and consumption determination | + | 0 | 0 | 0 | 0 | 0 | ++ | + | ++ | 2 | - | 1 | 0 | 0 | 0 | 0 | 0 | 2
| level 3 | Analysing, performance evaluation, benchmarking | + | 0 | 0 | 0 | 0 | 0 | +++ | + | + | 2 | - | 1 | 0 | 0 | 0 | 0 | 0 | 3
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | MC-6 | Reporting information regarding historical energy consumption |  | Service group: | Feedback - Reporting information | [8 empty] | line | 74
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Indication of actual values only (e.g. temperatures, meter values) | 0 | 0 | 0 | 0 | 0 | 0 | + | + | + | 4 | - | 0 | 0 | 0 | 0 | 0 | 0 | 1
| level 2 | Trending functions and consumption determination | + | 0 | 0 | 0 | 0 | 0 | ++ | + | + | 4 | - | 1 | 0 | 0 | 0 | 0 | 0 | 2
| level 3 | Analysing, performance evaluation, benchmarking | + | 0 | 0 | 0 | 0 | 0 | +++ | 0 | 0 | 4 | - | 1 | 0 | 0 | 0 | 0 | 0 | 3
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Information sources | [9 empty] | own judgment
Standard?
| code | service
► | MC-7 | Reporting information regarding predicted energy consumption |  | Service group: | Feedback - Reporting information | [8 empty] | line | 88
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Indication of actual values only (e.g. temperatures, meter values) | 0 | 0 | 0 | 0 | 0 | 0 | + | + | + | 4 | - | 0 | 0 | 0 | 0 | 0 | 0 | 1
| level 2 | Trending functions and consumption determination | + | 0 | 0 | 0 | 0 | 0 | ++ | + | + | 4 | - | 1 | 0 | 0 | 0 | 0 | 0 | 2
| level 3 | Analysing, performance evaluation, benchmarking | + | 0 | 0 | 0 | 0 | 0 | +++ | 0 | 0 | 4 | - | 1 | 0 | 0 | 0 | 0 | 0 | 3
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | MC-9 | Occupancy detection: connected services |  | Service group: | TBS interaction control | [8 empty] | line | 102
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | For individual functions, e.g. lighting | + | 0 | + | + | 0 | + | 0 | 0 | + | 5 | - | 1 | 0 | 1 | 1 | 0 | 1 | 0
| level 2 | Centralised detection which feeds in to several TBS such as lighting and heating | + | 0 | + | + | 0 | ++ | 0 | - | 0 | 5 | - | 1 | 0 | 1 | 1 | 0 | 2 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | MC-10 | Occupancy detection: space and activity |  | Service group: | TBS interaction control | [8 empty] | line | 116
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No occupancy detection present | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Occupancy detection can determine presence in room | + | 0 | 0 | 0 | 0 | 0 | 0 | + | ++ | 2 | - | 1 | 0 | 0 | 0 | 0 | 0 | 0
| level 2 | Occupancy detection can determine average number of people in space | + | 0 | + | 0 | + | 0 | 0 | + | ++ | 2 | - | 1 | 0 | 1 | 0 | 1 | 0 | 0
| level 3 | Occupancy detection can determine the actual number of people in a space | ++ | 0 | + | 0 | ++ | 0 | 0 | - | - | - | - | 2 | 0 | 1 | 0 | 2 | 0 | 0
| level 4 | Occupancy detection can determine position of people in space (e.g. behind desk) | ++ | 0 | ++ | 0 | ++ | 0 | 0 | - | - | - | - | 2 | 0 | 2 | 0 | 2 | 0 | 0
+
Information sources
Standard?
| code | service
► | MC-11 | Remote surveillance of building behaviour |  | Service group: | Central control of energy consumers | [8 empty] | line | 130
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Not present | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Remote control of main TBS | + | + | 0 | ++ | 0 | + | 0 | + | - | 1 | - | 1 | 1 | 0 | 2 | 0 | 1 | 0
| level 2 | Remote control of main TBS with centralised occupancy detection | ++ | + | 0 | ++ | 0 | + | 0 | - | 0 | 2 | - | 2 | 1 | 0 | 2 | 0 | 1 | 0
| level 3 | Remote control of main TBS with centralised occupancy detection, automatic non-occupancy default settings and user alerts | +++ | ++ | 0 | ++ | 0 | + | ++ | - | - | - | - | 3 | 2 | 0 | 2 | 0 | 1 | 2
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | MC-12 | Central off-switch for appliances at home |  | Service group: | Central control of energy consumers | [8 empty] | line | 144
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | simple off switch | + | + | 0 | + | 0 | + | 0 | + | - | 1 | - | 1 | 1 | 0 | 1 | 0 | 1 | 0
| level 2 | off switch with ability for remote operation | ++ | + | 0 | ++ | 0 | ++ | + | - | 0 | 2 | - | 2 | 1 | 0 | 2 | 0 | 2 | 1
| level 3 | secquence of deactivation for load optimisation | ++ | +++ | 0 | ++ | 0 | ++ | + | - | - | - | - | 2 | 3 | 0 | 2 | 0 | 2 | 1
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
► | MC-13 | Central reporting of TBS performance and energy use |  | Service group: | Feedback - Reporting information | [8 empty] | line | 158
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Real time indication of energy use per energy carrier | + | 0 | 0 | + | 0 | + | + | common | common | 1 | - | 1 | 0 | 0 | 1 | 0 | 1 | 1
| level 2 | Real time indication of sub-metererd energy use or other performance metrics for at least 2 domains | + | 0 | 0 | + | 0 | + | ++ | rare | rare | 2 | - | 1 | 0 | 0 | 1 | 0 | 1 | 2
| level 3 | Real time indication of sub-metererd energy use or other performance metrics for all main TBS | + | 0 | 0 | ++ | 0 | + | +++ | rare | rare | 5 | - | 1 | 0 | 0 | 2 | 0 | 1 | 3
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-14 | Power flows measurement and communications |  | Service group: | DSM- Grid | [8 empty] | line | 172
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | local use of sensor data | + | + | 0 | 0 | 0 | - | 0 | 0 | + | 5 | - | 1 | 1 | 0 | 0 | 0 | -1 | 0
| level 2 | use of sensor data in microgrid operations | + | ++ | 0 | 0 | 0 | - | 0 | 0 | + | 5 | - | 1 | 2 | 0 | 0 | 0 | -1 | 0
| level 3 | DSO based use of sensor data | 0 | ++ | 0 | 0 | 0 | - | 0 | 0 | -- | 5 | - | 0 | 2 | 0 | 0 | 0 | -1 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-15 | Energy delivery KPI tracking and calculation |  | Service group: | DSM - Local Systems | [8 empty] | line | 186
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | local optimisation | + | + | 0 | + | 0 | + | + | - | 0 | 10 | - | 1 | 1 | 0 | 1 | 0 | 1 | 1
| level 2 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Information sources | [9 empty] | own judgment
Standard?
| code | service
| MC-16 | Fault location and detection |  | Service group: | DSM- Grid | [8 empty] | line | 200
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | local based detection of errors | 0 | + | 0 | 0 | 0 | ++ | + | -- | 0 | 10 | - | 0 | 1 | 0 | 0 | 0 | 2 | 1
| level 2 | DSO optimised operations | 0 | + | 0 | 0 | 0 | ++ | + | -- | 0 | 10 | - | 0 | 1 | 0 | 0 | 0 | 2 | 1
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-17 | Fault prevention and risk assessment |  | Service group: | DSM- Grid | [8 empty] | line | 214
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | local based detection of errors | 0 | + | + | + | 0 | + | 0 | 0 | 0 | 5 | - | 0 | 1 | 1 | 1 | 0 | 1 | 0
| level 2 | DSO optimised operations | 0 | + | + | + | 0 | + | 0 | 0 | 0 | 5 | - | 0 | 1 | 1 | 1 | 0 | 1 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-18 | Fraud detection and losses calculation |  | Service group: | DSM- Grid | [8 empty] | line | 228
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | local based detection of errors | + | 0 | 0 | 0 | 0 | + | + | + | + | 2 | - | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 2 | DSO optimised operations | + | 0 | 0 | 0 | 0 | + | + | - | - | 5 | - | 1 | 0 | 0 | 0 | 0 | 1 | 1
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-19 | Neighbourhood energy efficiency calculation |  | Service group: | DSM - Local Systems | [8 empty] | line | 242
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | local optimization | + | + | 0 | 0 | 0 | - | 0 | 0 | + | 5 | - | 1 | 1 | 0 | 0 | 0 | -1 | 0
| level 2 | data exchange for local swarm and optimization | ++ | ++ | 0 | 0 | 0 | - | 0 | 0 | 0 | 5 | - | 2 | 2 | 0 | 0 | 0 | -1 | 0
| level 3 | data exchange for local swarm and optimization for DSP vpp control | ++ | ++ | 0 | 0 | 0 | - | 0 | 0 | 0 | 5 | - | 2 | 2 | 0 | 0 | 0 | -1 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
|  | Standard? | IEC TC 57 |  |  |  |  | IEC TC 57 | IEC TC 57
| code | service
| MC-20 | Demand prediction |  | Service group: | DSM- Grid | [8 empty] | line | 256
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | local optimization | + | + | 0 | + | 0 | - | 0 | + | ++ | 2 | - | 1 | 1 | 0 | 1 | 0 | -1 | 0
| level 2 | adaptive load forecast | + | + | 0 | + | 0 | - | 0 | + | ++ | 4 | - | 1 | 1 | 0 | 1 | 0 | -1 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-21 | Information exchange on renewables generation prediction |  | Service group: | DSM- Grid | [8 empty] | line | 270
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | local optimization | 0 | + | 0 | 0 | 0 | + | 0 | 0 | + | 2 | - | 0 | 1 | 0 | 0 | 0 | 1 | 0
| level 2 | adaptive load forecast | 0 | + | 0 | 0 | 0 | + | 0 | 0 | 0 | 2 | - | 0 | 1 | 0 | 0 | 0 | 1 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-22 | Heat management for a multi-tenant house by aggregator |  | Service group: | DSM- Storage | [8 empty] | line | 284
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | occupant best-effort | + | 0 | + | + | 0 | 0 | 0 | ++ | + | 5 | - | 1 | 0 | 1 | 1 | 0 | 0 | 0
| level 2 | building best-effort | ++ | 0 | + | + | 0 | 0 | 0 | + | ++ | 5 | - | 2 | 0 | 1 | 1 | 0 | 0 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-23 | DSM control of a device by an aggregator |  | Service group: | DSM - Local Systems | [8 empty] | line | 298
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | microgrid operations (energy based) | 0 | + | 0 | 0 | 0 | - | 0 | 0 | 0 | 2 | - | 0 | 1 | 0 | 0 | 0 | -1 | 0
| level 2 | VPP operations (price based) | 0 | + | - | - | 0 | - | 0 | 0 | 0 | 2 | - | 0 | 1 | -1 | -1 | 0 | -1 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-24 | Energy storage penetration prediction |  | Service group: | DSM- Storage | [8 empty] | line | 312
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | local forecast | + | ++ | 0 | 0 | 0 | - | 0 | 0 | + | 2 | - | 1 | 2 | 0 | 0 | 0 | -1 | 0
| level 2 | microgrid based forecast | + | ++ | 0 | 0 | 0 | - | 0 | 0 | + | 2 | - | 1 | 2 | 0 | 0 | 0 | -1 | 0
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-25 | Smart Grid Integration |  | Service group: | Smart Grid Integration | [8 empty] | line | 326
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None - No harmonization between grid and building energy systems; building is operated independently from the grid load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Building energy systems are managed and operated depending on grid load; demand side management is used for load shifting | 0 | +++ | 0 | 0 | 0 | 0 | 0 | 0 | + | 2 | - | 0 | 3 | 0 | 0 | 0 | 0 | 0
| level 2 | 0 | [10 empty] | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 3 | 0 | [10 empty] | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [10 empty] | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-26 | DSM control of equipment |  | Service group: | DSM control of equipment | [8 empty] | line | 340
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | Not present | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Smart appliances or DHW subject to DSM control | 0 | + | 0 | 0 | 0 | 0 | 0 | 0 | + | 2 | - | 0 | 1 | 0 | 0 | 0 | 0 | 0
| level 2 | Heating or cooling subject to DSM control | 0 | + | 0 | 0 | 0 | 0 | 0 | 0 | + | 2 | - | 0 | 1 | 0 | 0 | 0 | 0 | 0
| level 3 | Heating and cooling subject to DSM control | 0 | ++ | 0 | 0 | 0 | 0 | 0 | - | - | - | - | 0 | 2 | 0 | 0 | 0 | 0 | 0
| level 4 | Smart appliances, DHW, heating and cooling subject to DSM control | 0 | +++ | 0 | 0 | 0 | 0 | 0 | - | - | - | - | 0 | 3 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-27 | Connecting PV to DSO grid |  | Service group: | Connecting PV to DSO grid | [8 empty] | line | 354
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | none | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | simple feed-in | 0 | + | 0 | 0 | 0 | 0 | 0 | 0 | + | 2 | - | 0 | 1 | 0 | 0 | 0 | 0 | 0
| level 2 | CLS interface | 0 | ++ | 0 | 0 | 0 | 0 | 0 | 0 | + | 2 | - | 0 | 2 | 0 | 0 | 0 | 0 | 0
| level 3 | DSO controls | 0 | +++ | 0 | 0 | 0 | 0 | 0 | - | - | - | - | 0 | 3 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-28 | Reporting information regarding DSM |  | Service group: | Feedback - Reporting information | [8 empty] | line | 368
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | None | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | Reporting information on current DSM flows and controls | 0 | + | 0 | 0 | 0 | 0 | ++ | 0 | + | 2 | - | 0 | 1 | 0 | 0 | 0 | 0 | 2
| level 2 | Reporting information on current, historical and predicted DSM flows and controls | 0 | + | 0 | 0 | 0 | + | +++ | 0 | + | 2 | - | 0 | 1 | 0 | 0 | 0 | 1 | 3
| level 3 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 4 | 0 | [7 empty] | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
Information sources
Standard?
| code | service
| MC-29 | Override of DSM control |  | Service group: | Override control | [8 empty] | line | 382
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No DSM control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | default | default | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0
| level 1 | DSM control without the possibility to override this control by the occupant | 0 | ++ | -- | 0 | 0 | 0 | -- | 0 | + | 2 | - | 0 | 2 | -2 | 0 | 0 | 0 | -2
| level 2 | Manual override and reactivation | 0 | - | 0 | + | 0 | 0 | 0 | 0 | + | 2 | - | 0 | -1 | 0 | 1 | 0 | 0 | 0
| level 3 | Scheduled override of DSM control and reactivation | 0 | + | 0 | ++ | 0 | + | + | - | - | - | - | 0 | 1 | 0 | 2 | 0 | 1 | 1
| level 4 | Scheduled override of DSM control and reactivation with artificial intelligence | 0 | ++ | 0 | +++ | 0 | ++ | ++ | - | - | - | - | 0 | 2 | 0 | 3 | 0 | 2 | 2
Information sources
Standard?

## various
| Domain | VARIOUS
| code | service
► | VA-1 | Coming home - leaving home functions |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | none | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | mobile based | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 2 | -
| level 2 | RFID based | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 2 | -
| level 3 | 0 | - | - | - | - | - | - | - | - | - | - | -
| level 4 | 0 | - | - | - | - | - | - | - | - | - | - | -
Information sources
Standard?
| code | service
► | VA-2 | Inactivity recognition services |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | none | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | building based (movement activation) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | ++ | ++ | 5 | -
| level 2 | room based | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0 | 5 | -
| level 3 | electricity sensor based (behaviour) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | 0 | 5 | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
► | VA-3 | Multi-tenant access control for buildings without keys |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | none | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | mobile based | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -- | - | 3 | -
| level 2 | RFID based | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -- | 0 | 3 | -
| level 3 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
► | VA-4 | Occupants Wellbeing and health status monitoring services |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | none | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | Functionality levels to be defined | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -- | -- | 5 | -
| level 2 | Functionality levels to be defined | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -- | -- | 5 | -
| level 3 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
► | VA-5 | Dementia monitoring |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | none | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | Functionality levels to be defined, e.g. Appliance monitoring with alarms | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | + | 3 | -
| level 2 | Functionality levels to be defined, e.g. Appliance and person monitoring | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | + | 3 | -
| level 3 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | + | 3 | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
► | VA-8 | Rain water Collection |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | none | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | reducing sewage network prevent overflows | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 2 | Re-use to prevent waste fo freshwater resources | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 3 | 0 | - | - | - | - | - | - | - | - | - | - | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
► | VA-9 | Smoke detection |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | no smoke detection | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | smoke detectors | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 2 | smoke detectors, cross-linked | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 3 | 0 | - | - | - | - | - | - | - | - | - | - | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
► | VA-10 | Water leakage detection |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | no leakage detection | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | leakage detection | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 2 | smoke detectors, cross-linked | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 3 | 0 | - | - | - | - | - | - | - | - | - | - | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
► | VA-11 | Carbon Monoxide detecion |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | no CO detection | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | CO detection | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 2 | CO detection, cross-linked to other TBS, e.g. warning signals through lighting | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 3 | 0 | - | - | - | - | - | - | - | - | - | - | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
| VA-12 | Emergency notification services |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | simple alarm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | alarm with remote notification | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 2 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 3 | 0 | - | - | - | - | - | - | - | - | - | - | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
| VA-13 | Smart testing of emergency lighting |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | No emergency lighting | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | Emergency lighting with manual testing | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 2 | Emergency lighting with automatic testing | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 3 | Emergency lighting with automatic testing, connected to a centralised reporting system | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
| VA-14 | Intelligent alerting on building events |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | none | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level 1 | basic technology | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 2 | Artificial Intelligence | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 3 | 0 | - | - | - | - | - | - | - | - | - | - | -
| level 4 | 0 | [7 empty] | - | - | - | -
Information sources
Standard?
| code | service
| VA-18 | Energy Cost Allocation for heating, cooling and water |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | no energy cost allocation | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level1 | heat cost allocators (HCA) / meters (M) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level2 | HCA / M remote reading walk by | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 3 | HCA / M remote reading smartphone | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 4 | HCA / M remote reading continuous information | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
Information sources
Standard?
| code | service
| VA-19 | Lift and elevator control and dispatching |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | simple on demand | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level1 | grouping calls | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level2 | forecasting | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 3 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 4 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
Information sources
Standard?
| code | service
| VA-20 | Lift and elevator monitoring and maintenance |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level2 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 3 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 4 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
Information sources
Standard?
| code | service
| VA-21 | Lift and elevator energy revovery |  | Service group: | #N/A
| Functionality levels |  | IMPACTS | [6 empty] | market uptake / TRL |  | Inspection time [minutes] | Preconditions / supporting technologies and services
|  |  | Energy savings on site | Flexibility for the grid and storage | Comfort | Convenience | Wellbeing and health | maintenance & fault prediction | information to occupants | residential | non-residential
| level 0 | none | N/A | N/A | N/A | N/A | N/A | N/A | N/A | default | default | 0 | -
| level1 | present | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level2 | energy recovery with capacitor or storage | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 3 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
| level 4 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | - | - | - | -
Information sources
Standard?

## _general (hidden)
building type |  | residential | non_residential | triage | Yes | No
|  | single-family house | office |  |  | Yes, mandatory
|  | small multi-family house | educational |  |  | No, not mandatory
|  | large multi-family house | healthcare
|  | other | other
HEATING
|  |  |  | emission type | TABS (Thermally Activated Building System)
EU countries |  | Austria | West Europe |  | Other hydronic system (e.g. radiators)
|  | Belgium | West Europe |  | Non-hydronic system (e.g. all-air)
|  | Bulgaria | South-East Europe
|  | Croatia | South-East Europe | production type | District heating
|  | Cyprus | South Europe |  | Heat Pump
|  | Czech Republic | North-East Europe |  | Central heating - combustion
|  | Denmark | North Europe |  | Central heating - other
|  | Estonia | North-East Europe |  | Decentral heating (e.g. stoves)
|  | Finland | North Europe
|  | France | West Europe | storage present? | Storage present
|  | Germany | West Europe |  | No storage present
|  | Greece | South Europe
|  | Hungary | South-East Europe | multiple heat gen? | Single generator
|  | Iceland | North Europe |  | Multiple generators
|  | Ireland | West Europe | DHW
|  | Italy | South Europe | production type | Non-electric
|  | Latvia | North-East Europe |  | Electric (direct or integrated heat pump)
|  | Liechtenstein | West Europe
|  | Lithuania | North-East Europe | Storage present | Storage present
|  | Luxembourg | West Europe |  | No storage present
|  | Malta | South Europe
|  | Netherlands | West Europe | Solar | Solar collector present
|  | Norway | North Europe |  | No solar collector present
|  | Poland | North-East Europe
|  | Portugal | South Europe | COOLING
|  | Romania | South-East Europe | emission type | TABS (Thermally Activated Building System)
|  | Slovakia | North-East Europe |  | Other hydronic system (e.g. radiators)
|  | Slovenia | South-East Europe |  | Non-hydronic system (e.g. all-air)
|  | Spain | South Europe
|  | Sweden | North Europe | storage present? | Storage present
|  | Switzerland | West Europe |  | No storage present
|  | United Kingdom | West Europe
|  | non EU | please use user defined weightings! | multiple heat gen? | Single generator
Multiple generators
VENTILATION
floor area |  | <200 m² |  | system type | Mechanical ventilation
|  | 200 - 500 m² |  |  | Controlled natural ventilation
500 - 1.000 m²
1.000 - 10.000 m²
|  | 10.000 - 25.000 m² |  | subtype | All-air
|  | > 25.000 m² |  |  | Combined air-water
Other
age |  | < 1960
|  | 1960 - 1990 |  | Heat recovery? (mechanical only) | Heat recovery
|  | 1990 - 2010 |  |  | No heat recovery
> 2010
not yet constructed
renovated |  | Renovated
|  | Original |  | Space heating | Used for space heating
Not used for space heating
weightings |  | Default
|  | User-defined |  | DYNAMIC ENVELOPE
|  |  |  | shades? | Present
rows to add to find the right weighting |  |  |  |  | Not present
heating | 5
dhw | 6 |  |  | ELECTRICITY
cooling | 7
ventilation | 8 |  |  | Local energy gen | On-site renewable electricity generation
lighting | 9 |  |  |  | No on-site renewable electricity generation
electricity | 10
DE | 11 |  |  | Storage? | Storage present
EV | 12 |  |  |  | No storage present
MC | 13
|  |  |  | CHP | CHP
column to find right weighting factor |  |  |  |  | No CHP
North Europe | 1
West Europe | 11 |  |  | EV
South Europe | 21 |  |  | on-site parking | On-site parking
North-East Europe | 30 |  |  |  | No on-site parking
South-East Europe | 39
|  |  |  | EV charging | EV charging
Error message |  |  |  |  | No EV charging
please enter a valid functionality level
heating | 44
DHW | 45
cooling | 46
ventilation | 47
lighting | 48
DE | 49
Electricity | 50
EV | 51